## GIKONDO SUBSTATION
GIKONDO
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-001 | PTR-1-001
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GIK-001 | GIK-001
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | SGB | SGB
| CountryOfManufacturer | Text | GERMANY | GERMANY
| ManufacturerYear | Short Integer | 1983 | 1983
| Year_commissioning | Short Integer | 1983 | 1983
| Owner | Short Integer | REG | 1 | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 15 MVA | 15
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 78.7A | 78.7
| SecondaryCurrent_A | Double | 551.8A | 551.8
| TertiaryCurrent_A | Double | NA | 0 | No Domain Code is proposed
| Vector_Group_Trx | Short Integer | YNyn0 | 19
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 6% | 0.06
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 20kW | 20
| LoadLosses | Double | 90kW | 90
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | MSIII3004 | MSIII3005
| TappingRange | Double | 110±16% |  | REG (This Should be a Text or create a Domain code)
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2020 | 2020
| SerialNumber | Text | 2189097 | 2189097
| Barcode | Text | NA
| TotalWeight | Double | 37500kg | 37500
| WeightOfActivePart | Double | 16500kg | 16500
| WeightOfOil | Double | 11000kg | 11000
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double | 3.665m | 3.665m
| Depth | Double
| Width | Double | 3.150m | 3.150m
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-2-001 | PTR-2-002
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GKND-001 | GKND-002
| PowerPlantname | Text
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | ALSTHOM | ALSTHOM
| CountryOfManufacturer | Text | FRANCE | FRANCE
| ManufacturerYear | Short Integer | 1986 | 1986
| Year_commissioning | Short Integer | 1986 | 1986
| Owner | Short Integer | REG | 1 | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 15 MVA | 15
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | NA | 0 | No Domain Code is proposed
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 78.7A | 78.7
| SecondaryCurrent_A | Double | 551.8A | 551.8
| TertiaryCurrent_A | Double | NA | 0
| Vector_Group_Trx | Short Integer | YNyn0 | 19
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 6% | 0.06
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 20kW | 20
| LoadLosses | Double | 90kW | 90
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | MSIII3004 | MSIII3004
| TappingRange | Double | 110±16% |  | REG (This Should be a Text or create a Domain code)
| Tap_changer_manufacturer | Text | MR | MR
| Tap_changer_country_orgin_ | Text | GERMANY | GERMANY
| TapChangerManufacturingDate | Short Integer | 2020 | 2020
| SerialNumber | Text | 238037.01 | 2189097
| Barcode | Text | NA
| TotalWeight | Double | 32000kg | 32000
| WeightOfActivePart | Double | 11900kg | 11900
| WeightOfOil | Double | 10500kg | 10500
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double |  | 3.665m
| Depth | Double
| Width | Double |  | 3.150m
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-3-001 | PTR-3-002
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GKND-001 | GKND-002
| PowerPlantname | Text
| TransformerNaming | Short Integer | TR3 | 2
| Manufacturer | Text | CHINT | CHINT
| CountryOfManufacturer | Text | CHINA | CHINA
| ManufacturerYear | Short Integer | 2010 | 2010
| Year_commissioning | Short Integer | 2010 | 2010
| Owner | Short Integer | REG | 1 | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 15 MVA | 15
| Primaryvoltage__kv | Double | 110 kV | 110
| Secondaryvoltage__kv | Double | 15kV | 15
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 78.7A | 78.7
| SecondaryCurrent_A | Double | 551.8A | 551.8
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | YNyn0 | 19
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3 | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 6% | 0.06
| NoLoadCurr_Percentage | Double | 10% | 0.1
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2 | 2
| No_Load_losses | Double | 20kW | 20
| LoadLosses | Double | 90kW | 90
| AltitudeLevel | Double | 2000m | 2000
| Noiselevel_db | Double | 75dB | 75
| NumberOfTappingPosition | Short Integer | 27 | 27
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | SHM-I | SHM-I
| TappingRange | Double | 110±16% | 110±16%
| Tap_changer_manufacturer | Text | CHINT | CHINT
| Tap_changer_country_orgin_ | Text | CHINA | CHINA
| TapChangerManufacturingDate | Short Integer | 2020
| SerialNumber | Text | M100322
| Barcode | Text | NA
| TotalWeight | Double | 49300kg
| WeightOfActivePart | Double | 17765kg
| WeightOfOil | Double | 16600kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double | Not provided
| Depth | Double | Not provided
| Width | Double | Not provided
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | AUX-TR1-001 | AUX-TR1-002
| PowerPlantID | Text | NA | NA
| Substation_ID | Text | GKND-001 | GKND-002
| PowerPlantname | Text | NA | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | FRANCE TRANSFO | FRANCE TRANSFO
| CountryOfManufacturer | Text | FRANCE | FRANCE
| ManufacturerYear | Short Integer | 1987 | 1988
| Owner | Short Integer | REG | 1
| Primaryvoltage__kv | Double | 15kV | 15
| Secondaryvoltage__kv | Double | 0.4kV | 0.4
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 9.6A | 9.6
| SecondaryCurrent_A | Double | 361A | 361
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | Dy5 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | (1U-1V-1W) (2U-2U-2W)
| WorkingCondition | Short Integer | Unknown, | 0
| PercentageImpedance | Double | 4%
| No_Load_losses | Double | 2kW
| LoadLosses | Double | 0.5KW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 55dB
| NumberOfTappingPosition | Short Integer | 3
| Standard_Code | Text | IEC 76
| Tap_changer | Short Integer | OFF LOAD
| VoltageVariationRange1 | text | 15±2.5%
| Tap_changer_manufacturer | Text | FRANCE TRANSFO
| Tap_changer_country_orgin_ | Text | FRANCE
| TapChangerManufacturingDate | Short Integer | 1987
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text | NA
| TotalWeight | Double | 950kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 210kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| WeightOfAccessories | Double | Not provided
| LV_CB_A | Short Integer | 400A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 1987
Earthing Transformer | transfomerID | Text | AUX-TR2-001
| PowerPlantID | Text | NA
| Substation_ID | Text | GKND-001
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1 | 1
| Manufacturer | Text | UNELEC
| CountryOfManufacturer | Text | FRANCE
| ManufacturerYear | Short Integer | 1974
| Owner | Short Integer | REG | 1
| Primaryvoltage__kv | Double | 15kV
| Secondaryvoltage__kv | Double | 0.4kV
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 9.6A
| SecondaryCurrent_A | Double | 361A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | Dy5 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | (1U-1V-1W) (2U-2U-2W)
| WorkingCondition | Short Integer | Unknown, | 0
| PercentageImpedance | Double | 4.19%
| No_Load_losses | Double | 2kW
| LoadLosses | Double | 0.5KW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 55dB
| NumberOfTappingPosition | Short Integer | 3
| Standard_Code | Text | UTE . CEI
| Tap_changer | Short Integer | OFF LOAD
| VoltageVariationRange1 | text | 15±2.5%
| Tap_changer_manufacturer | Text | UNELEC
| Tap_changer_country_orgin_ | Text | FRANCE
| TapChangerManufacturingDate | Short Integer | 1974
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text | NA
| TotalWeight | Double | 1060kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 230kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| WeightOfAccessories | Double | Not provided
| LV_CB_A | Short Integer | 400A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 1974
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | GKND-001
| Busbar_HV_ID | Text | BB-001
| Number_of_Busbar_HV | Short Integer | 2
| Number_of_Busbar_MV | Short Integer | 2
| Type_of_Busbar | Short Integer | Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 1
| Barcode | Short Integer | NA
| Operating_Voltage_Level_kV | Double | 110kV
| Short_circuit_current_kA | Double | 50kA
| Nominal_Current_A | Double | 960A
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J01
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117021
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J02
| FeederName | Text | INCOMER RENTAL POWER
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J03
| FeederName | Text | NYARURAMA
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J04
| FeederName | Text | KIMIHURURA
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J05
| FeederName | Text | KIGALI NORD
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J06
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J07
| FeederName | Text | AUXILIARY TRANSFORMER 1
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J08
| FeederName | Text | BUS COUPLER
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J09
| FeederName | Text | INCOMER TR3
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J10
| FeederName | Text | AUXILIARY TRANSFORMER 2
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J11
| FeederName | Text | KIGALI SOUTH
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J12
| FeederName | Text | PARC INDUSTRIEL
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J13
| FeederName | Text | GASOGI
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J14
| FeederName | Text | CAPACITOR BANK
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J15
| FeederName | Text | GIKONDO HAUT
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J16
| FeederName | Text | INCOMER TR2
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1VB2117022
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J17
| FeederName | Text | MINISTERE 1
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1YHP000068A1351
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J18
| FeederName | Text | MINISTERE 2
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1YHP000068A1352
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | GKND-001
| FeederID | Text | J19
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Outgoing feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2007
| Serial_Number | Text | 1YHP000068A1353
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2007
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 15KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 2000A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
Line Bay | Line_Bay_ID | Text | E01
| Substation_ID | Text | GKND-001
| Line_Bay_Name | Text | JABANA
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 542plus
Line Bay | Line_Bay_ID | Text | E02
| Substation_ID | Text | GKND-001
| Line_Bay_Name | Text | MONT KIGALI
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 542plus
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-1
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-2
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-3
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-4
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-5
| Substation_ID | Text | GKND-001
| Manufacturer | Text | TRENCH
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-6
| Substation_ID | Text | GKND-001
| Manufacturer | Text | MEHRU
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT1-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-009
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT1-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-010
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT1-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-011
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT2-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-005
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT2-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-004
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT2-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/010-001
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT3-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/3
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT3-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/6
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT3-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/1
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT4-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/2
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT4-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/4
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GEC ALSTHOM
| Current Transfomer ID | Text | CT4-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | SWEDEN
| ManufacturerYear | Double | 1995
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 25-50-100A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | MA85100/5
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | AREVA T&D
| Current Transfomer ID | Text | CT5-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Double | 2010
| Standard_Code | Text | IEC 60044
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -40°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2010/483678
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | AREVA T&D
| Current Transfomer ID | Text | CT5-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Double | 2010
| Standard_Code | Text | IEC 60044
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -40°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2010/483679
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | AREVA T&D
| Current Transfomer ID | Text | CT5-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Double | 2010
| Standard_Code | Text | IEC 60044
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -40°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2010/483680
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT6-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/040-003
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT6-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/040-008
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | TRENCH
| Current Transfomer ID | Text | CT6-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Double | 2013
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 100-200A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 27370/040-010
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 10305-20-2035520/4
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 10305-20-2035520/3
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 10305-20-2035520/6
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB4
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 10305-20-2035520/5
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB5
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 8328-10-2032913/1
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | ALSTHOM
| CircuitBreakerID | Text | CB6
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Short Integer | 2013
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 10305-10-2035520/2
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-1
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-2
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-3
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-4
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-4
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-5
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-5
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-6
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q2-6
| Substation | Text | GKND-001
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2012
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | Substation_Name | Short Integer | GIKONDO
| Substation_ID | Text | GKND-001
| Substation_Total_Capacity_MVA | Double | 45MVA
| Substation_Voltage_Level_kV | Short Integer | 110/15kV | 9
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 3
| Numbe_of_Earthing_Transfomer | Short Integer | 0
| Number_Distribution_Transf | Short Integer | 0
| Number of auxiliary transformers | Short Integer | 2 | 1
| Standby_Generators | Short Integer | YES
| Busbar_Configuration_HV | Short Integer | Double busbar | 2
| Number of MV Feeders | Short Integer | 19
| Number of HV line Bays | Short Integer | 2
| Number of Trx Bays | Short Integer | 3
| Configuration_Busbar_MV | Short Integer | Double busbar | 2
| BuscouplerHV | Short Integer | YES | 1
| BuscouplerMV | Short Integer | YES | 1
| Type_of_Busbar_HV | Short Integer | Tubular | 2
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 1974
| Year_of_upgrade | Short Integer | 1987 & 2013
| Contractor_Name | Text | SGEEM-GTME-TAKAOKA
| Substation_Meter_SN | Text | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES, | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-1
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-2
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-3
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2013
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
DC Supply 48 VDC Battery | Manufacturer | Text
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V
| RatedVoltage | Double | 48V
| TenHrsRatingCapacity | Double | 60Ah
| One_min_rating_Current_A | Double
| MaximumVolatge_V | Double | 48+15%
| MinimumVoltage_V | Double | 48-15%
| MinimumVoltageperCell | Double | 1.2V
| NumberofCells | Short Integer | 40
| BatteryFloatingVoltage | Double | 50
| BoostChargingVoltage | Double | 55.8V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 60A
| SelfDischargeat_25oC | Double | 7%
| TypeofCooling | Text | Natural
| Charging time (hrs) | Double | 5hrs
DC Supply 110 VDC Battery | Manufacturer | Text | AEG
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| Model | Text | KM 185 P/N
| Type | Short Integer | NiCd
| Standards_ | Text | DIN 41772
| RatedVoltage | Double | 110V
| TenHrsRatingCapacity | Double | 185Ah
| One_min_rating_Current_A | Double | 100A
| MaximumVolatge_V | Double | 110+15%
| MinimumVoltage_V | Double | 110-15%
| MinimumVoltageperCell | Double | 1.02V
| Number_of_cells__No_ | Long Integer | 90
| BatteryFloatingVoltage | Double | 112.5V
| BoostChargingVoltage | Double | 132.3V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 100A
| TypeofCooling | Short Integer | Natural
DC Supply 48 VDC charger | Manufacturer | Text | AEG GmbH
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| Model | Text | Profitec 2000 S 48V/60A
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 5.53kVA
| DC Output (Kw) | Double | 2.88kW
| DC_Output_kV | Double | 48V
| Rated_output_Voltage_V | Double | 48V
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ
| OperatingConditions | Text
| Altitude_m | Double | 2000m
| Degree_protection_ | Short Integer | IP 20 | 55
| DCDistributionBoard | Short Integer | No | 0
| RatedCurrent_A | Double | NA
| NumberofFeeders | Short Integer | NA
| short_circuit_capacity_breaker | Double | NA
DC Supply 110 VDC charger | Manufacturer | Text | AEG
| Substation_ID | Text | GKND-001
| CountryOfManufacturer | Text | GERMANY
| Model | Text | Profitec 2000 S 110V/100A
| TypeofOperation | Short Integer | Parallel
| Charger_type | Short Integer | Thyristor controlled
| Standards_ | Text | DIN VDE 0558
| ChargingTime | Double | 5h
| Frequency_Hz | Short Integer | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 17.3kVA
| VoltageVariation | Double | ±5%
| DC_Output_kV | Double | 110V
| TypeofCharging | Text | Float/ Boost
| Rated_output_Voltage_V | Double | 110V
| MaximumDC_Voltage_V | Double | 126V
| ConstantVoltageAccuracy | Double | ±10%
| Rated_DC_output_Current_A | Double | 100A
| FloatingVoltageRegulatin | Double | 104.4V
| EqualisingVoltageRegulatin | Double | 128.8V
| Minimum_Insulation_resistance_ | Double | 5MΏ
| TypeofCooling | Short Integer | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C
| Altitude_m | Double | >1000m
| Total_Weight_Charger_kg | Double | 340kg
| Degree_protection_ | Short Integer | IP20
| RatedCurrent_A | Double | 100A
| ShortCircuitStrength_kA_sec | Double | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate, Others
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE
| Type | Text | REASON DR60
| Standards | Text | IEC61850
| Arrangement | Short Integer | Panel mounted | 2
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A
| Nominal_voltage_Vdc | Double | 110DC
| Power_consumption_VA | Double | 150VA
| NumberofAnalogInputs | Short Integer | 32
| NumberofBinaryInputs | Short Integer | 96
| NumberofBinaryOutputs | Short Integer | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | JABANA
| Year_of_commisioning | Short Integer | 1974
| ContractorName | Text | SGEEM
| Manufacturer | Text | 1972
| Voltage_Level_kV | Short Integer | 2 | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR,CU | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 8.4km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 130kN
| MaxElectricResitance | Double | 0.119(Ώ/km)
| PositiveSequenceReactance | Double | 0.427(Ω/km)
| PositiveSequenceResistance | Double | 0.123(Ω/km)
| ZeroSequenceResistance | Double | 0.327(Ω/km)
| ZeroSequenceReactance | Double | 1.119(Ω/km)
| ZeroSequenceCapacitance | Double | 0.011(µf/km)
| PositiveSequenceCapacitance | Double | 0.0066(µF/km)
High Voltage Line | Name | Text | MONT KIGALI
| Year_of_commisioning | Short Integer | 1974
| ContractorName | Text | SGEEM
| Manufacturer | Text | 1972
| Voltage_Level_kV | Short Integer | 2 | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR,CU | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 5.2km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 130kN
| MaxElectricResitance | Double | 0.119(Ώ/km)
| PositiveSequenceReactance | Double | 0.427(Ω/km)
| PositiveSequenceResistance | Double | 0.123(Ω/km)
| ZeroSequenceResistance | Double | 0.327(Ω/km)
| ZeroSequenceReactance | Double | 1.119(Ω/km)
| ZeroSequenceCapacitance | Double | 0.011(µf/km)
| PositiveSequenceCapacitance | Double | 0.0066(µF/km)
Transformer Bay | Trx_Bay_ID | Text | E03
| Substation_ID | Text | GKND-001
| Trx_Bay_Name | Text | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 15MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SIEMENS - 7UT612
| Type_of_Back_up_relay | Text | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+
Transformer Bay | Trx_Bay_ID | Text | E03
| Substation_ID | Text | GKND-001
| Trx_Bay_Name | Text | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 15MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SIEMENS - 7UT612
| Type_of_Back_up_relay | Text | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+
Transformer Bay | Trx_Bay_ID | Text | E03
| Substation_ID | Text | GKND-001
| Trx_Bay_Name | Text | TRANSFORMER 3
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 15MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SIEMENS - 7UT612
| Type_of_Back_up_relay | Text | Included in 7UT612
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB
| CircuitBreakerID | Text | CB-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | VD4X 4012-25
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 2000A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB
| CircuitBreakerID | Text | CB-MV2
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | VD4X 4012-25
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 2000A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB
| CircuitBreakerID | Text | CB-MV3
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | VD4X 4012-25
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 1250A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | WTW
| CurrentTransfomer_ID | Text | CT-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | EVEG-36-34
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1-1A
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV
| LimitsContPrimaryCurrency_A | Double | 120%
Indoor Current Transformer | Manufacturer | Text | ABB
| CurrentTransfomer_ID | Text | CT-MV2
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | EVEG-36-34
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 1
| Rated_Primary_Current_A | Double | 1600A
| Rated_Secondary_Current | Double | 150mV
| AccuracyClass | Text | Cl 1
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV
| LimitsContPrimaryCurrency_A | Double | NA
Indoor Current Transformer | Manufacturer | Text | WTW
| CurrentTransfomer_ID | Text | CT-MV3
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | ASG-36-5
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 3
| Rated_Primary_Current_A | Double | 80-240-640A
| Rated_Secondary_Current | Double | 150mV
| AccuracyClass | Text | Cl 1
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV
| LimitsContPrimaryCurrency_A | Double | NA
Indoor Voltage Transformer | Manufacturer | Text | WTW
| VoltageTransfomer_ID | Text | VT-MV1
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | EVEG-36-0.5
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV
| RatedImpulseWithstandVol | Double | 170kV
| RatedPrimaryVoltage_kV | Double | 15-30kV/√3
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 15VA
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | WTW
| VoltageTransfomer_ID | Text | VT-MV2
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | EVEG-36-0.5
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV
| RatedImpulseWithstandVol | Double | 170kV
| RatedPrimaryVoltage_kV | Double | 15-30kV/√3
| Rated_secondary_voltage_winding_1__V_ | Text | 100V/√3
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 15VA
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-001
| Substation_ID | Text | GKND-001
| Bay_ID | Text | E01
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | 2010
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | RS 485
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-2-001
| Substation_ID | Text | GKND-001
| Bay_ID | Text | E02
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E02
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | 2010
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Transformer Protection | RelayType | Text | SIEMENS-7UT612
| Bay_ID | Text | E03
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Transformer Protection | RelayType | Text | SIEMENS-7UT612
| Bay_ID | Text | E04
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Transformer Protection | RelayType | Text | SIEMENS-7UT612
| Bay_ID | Text | E05
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E02
| Substatoin_ID | Text | GKND-001
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Standby Generator | Manufacturer | Text | GREEN POWER
| Substation_ID | Text | GKND-001
| Standby_Generator_ID | Text | DGU-1-001
| CountryOfManufacturer | Text | ITALY
| Mode_Operation | Short Integer | Prime / Standby
| Model | Text | GP250 S/I-N-A
| Type_Assembly | Short Integer | Generating set ISO 8528
| Arrangement | Short Integer | Sound proof
| Phases | Short Integer | 3
| RatedOuptuPower_kVA | Double | 250kVA
| RatedVoltage | Double | 230/400V
| RatedCurrent_A | Double | 360A
| PowerFactor | Double | 0.8
| CouplingofEngine | Text | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Perkins
| Governor | Text | PID
| GobernorBrand | Text | Datakom (DKG)
| RatedPower_kVA_kW | Double | 250kVA
| CompressionRatio_ | Text | 15:01
| NoofCylinder | Short Integer | 6
| Speed_RPM | Double | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500L
| Cooling_System | Short Integer | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 96dB
| LubricationOilConsumption | Double | 0.025L/h
| Ambient_temperature | Double | Minus 20 0C up to Plus 40 0C
| Protection index | Text | IP44
| MethodofStarting | Text | Man/Auto
| Voltage_VDC | Double | 24V
| Power_kW | Double | 200kW
| Battery_Capacity_Ah | Double | 135Ah
| BatteryType | Text | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50Hz | 50
| VoltageRegulationMode | Short Integer | AVR
| Total_Weight | Double | 2200kg