## GISAGARA
GISAGARA
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-039
| PowerPlantID | Text | NA
| Substation_ID | Text | GSGR-039
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | 0 | 0
| Manufacturer | Text | CHINA ZUTCO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2021
| Year_commissioning | Short Integer | 2021
| Owner | Short Integer |  |  | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 20
| Primaryvoltage__kv | Double | 220
| Secondaryvoltage__kv | Double | 30
| TertiaryCurrent_A | Short Integer | 0 | 0
| Nominal_Frequency | Short Integer | 50 | 50
| PrimaryCurrent_A | Double | 52.5
| SecondaryCurrent_A | Double | 385.3
| TertiaryCurrent_A | Double | 0
| Vector_Group_Trx | Short Integer | 19 | 14
| CoolingMethod | Short Integer | 1 | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | 2 | 2
| PercentageImpedance | Double | 0.11
| NoLoadCurr_Percentage | Double | 0.1
| Winding_Material | Short Integer | 1 | 1
| Number_windings | Short Integer | 2
| No_Load_losses | Double | 10
| LoadLosses | Double | 55
| AltitudeLevel | Double | 2000
| Noiselevel_db | Double | 75
| NumberOfTappingPosition | Short Integer | 17
| TapChangerType | Short Integer | 1 | 1
| TapChangerModel | Text | CM2III 500Y/72.5C-10193W
| TappingRange | Double |  |  | 110±16% (This can not be a single Number because it is plus/minus)
| Tap_changer_manufacturer | Text | SMS
| Tap_changer_country_orgin_ | Text | CHINA
| TapChangerManufacturingDate | Short Integer | 2021
| SerialNumber | Text | CM2200011
| Barcode | Text | NA
| TotalWeight | Double | 83640 |  | Unit in kg missing
| WeightOfActivePart | Double |  |  | Unit in kg missing
| WeightOfOil | Double | 29300 |  | Unit in kg missing
| WeightOfUpperTank | Double |  |  | Unit in kg missing
| TransportationOfWeight_N2 | Double |  |  | Unit in kg missing
| Height | Double |  |  | unit in m missing
| Depth | Double |  |  | unit in m missing
| Width | Double |  |  | unit in m missing
| Bushing_Material | Short Integer | 1 | 1
Earthing Transformer | transfomerID | Text | ETR-1-039
| PowerPlantID | Text | NA
| Substation_ID | Text | GSGR-039
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | 0 | 0
| Manufacturer | Text | ZHE -JIANGSHAN TRANSFRMER CO.LTD
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2021
| Owner | Short Integer | 1 | 1
| Primaryvoltage__kv | Double | 30
| Secondaryvoltage__kv | Double | 0.4
| TertiaryCurrent_A | Short Integer
| Nominal_Frequency | Short Integer | 50 | 50
| PrimaryCurrent_A | Double | 6
| SecondaryCurrent_A | Double | 455.2
| TertiaryCurrent_A | Double
| Vector_Group_Trx | Short Integer | YNz5 | 20
| CoolingMethod | Short Integer | 1 | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | 2 | 2
| PercentageImpedance | Double | 0.4
| No_Load_losses | Double | 0.9 |  | Unit missing in kW
| LoadLosses | Double | 4.5 |  | Unit missing in kW
| AltitudeLevel | Double | 2000 |  | Unit missing in m
| Noiselevel_db | Double | 55
| NumberOfTappingPosition | Short Integer | 5
| Standard_Code | Text | IEC 60076
| Tap_changer | Short Integer
| VoltageVariationRange1 | text | 15±2.5%
| Tap_changer_manufacturer | Text | ZHE -JIANGSHAN TRANSFRMER CO.LTD
| Tap_changer_country_orgin_ | Text | CHINA
| TapChangerManufacturingDate | Short Integer | 2021
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text
| TotalWeight | Double | 4540 |  | Unit in kg missing
| WeightOfActivePart | Double |  |  | Unit in kg missing
| WeightOfOil | Double | 1385 |  | Unit in kg missing
| WeightOfUpperTank | Double |  |  | Unit in kg missing
| TransportationOfWeight_N2 | Double |  |  | Unit in kg missing
| WeightOfAccessories | Double |  |  | Unit in kg missing
| LV_CB_A | Short Integer | 630A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 2021
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | GSGR-039
| Busbar_HV_ID | Text | BB-039
| Number_of_Busbar_HV | Short Integer | 1
| Number_of_Busbar_MV | Short Integer | 1
| Type_of_Busbar | Short Integer | 2xString Conductor ACSR 240/40mm2 |  | Domain is missing for Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | ACSR | 3
| Barcode | Short Integer | NA
| Operating_Voltage_Level_kV | Double | 220kV
| Short_circuit_current_kA | Double | 40kA
| Nominal_Current_A | Double | 908A
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H01
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Incomer Feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000020/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H02
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000030/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H03
| FeederName | Text | HUYE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000040/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 1
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H04
| FeederName | Text | SAVE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000050/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 1
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H05
| FeederName | Text | SPARE
| PanelFunction | Short Integer | Line Feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | T-Type | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000060/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 1
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-039
| Substation_ID | Text | GSGR-039
| FeederID | Text | H06
| FeederName | Text | BUSBAR VT
| PanelFunction | Short Integer | Line Feeder | 1
| SwitchingDevices | Short Integer | Isolator only | 1
| Type_of_MV_cable_termination | Short Integer | NA | 2
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2021
| Serial_Number | Text | CV966736-000070/1
| Manufacturer | Text | SIEMENS
| Year_of_Commissioning | Short Integer | 2021
| Country_origin | Text | GERMANY
| Type_Model | Text | 8DA10
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30kV
| Standards | Text | IEC 622271-203
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | SIEMENS - 7SA82 |  | SIEMENS - 7SA82 (This should be a Text)
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 70kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 50kPa
| Smart_meter_Installed | Short Integer | 0 | 0
| Meter_number___if_yes_ | Text | Not existing
Line Bay | Line_Bay_ID | Text | D01
| Substation_ID | Text | GSGR-039
| Line_Bay_Name | Text | KIGOMA
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 1
| Line_Bay_Capacity_MVA | Double | 40MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | ABB-RED670
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | Including in RED 670
| Type_of_BCU_Bay_control_unit | Text | SIEMENS-6MD85
Line Bay | Line_Bay_ID | Text | D02
| Substation_ID | Text | GSGR-039
| Line_Bay_Name | Text | NGOZI
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6 | Others (110kV)
| Line_Bay_Capacity_MVA | Double | 40MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | ABB-RED 670
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | Including in RED 670
| Type_of_BCU_Bay_control_unit | Text | SIEMENS-6MD85
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3
| Substation_ID | Text | GSGR-039
| Manufacturer | Text | MEHRU EME
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 61869-3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitive | 1
| AltitudeLevel | Double | 2000m |  | Unit in m is missing
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 75VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | This should be a Text -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s |  | This should be a Text 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT1-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/1/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT1-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/4/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT1-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC8344/1/5/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT2-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC 8344/7/1/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT2-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC 8344/7/6/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT2-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 400-800A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC 11606/1/1/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT3-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 200-100A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC8344/2/3/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT3-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 200-100A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | OC8344/2/2/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
Current Transformer | Manufacturer | Text | MEHRU EME
| Current Transfomer ID | Text | CT3-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC61896-2
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 1.2
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C |  | -25°C/+40°C(This shouldbe aText)
| RatedVoltageFactor | Double
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A |  | 200-100A (The CT has twocores and thisshould be a Text)
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 40kA
| Rated_Peak_Short_Cir_Current | Double | 100kA |  | Unit in kA is missing
| KneePoint_V | Double
| SerialNumber | Text | 0C8344/2/1/21
| SF_ALF | Text | 20
| LimitsContPrimaryCurrency_A | Double | 1.2
| PowerFrequencyTestVoltage_kV | Double | 275kV
| Insulator | Short Integer | Oil | 1
| Degree_of_Protection | Text | IP55
| RatedContThermCurrentFactor_A | Double | 1.2
| DurationofShortCircuit_s | Double | 3
| AltitudeLevel | Double | 2000
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D
| CircuitBreakerID | Text | CB1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2019
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | "32710051390010001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double |  |  | This should be a Text -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer |  |  | REG This should be a text or create a Domain code
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg |  | Unit in kg is missing
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D
| CircuitBreakerID | Text | CB2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2019
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | "32710051390010002
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE T&D
| CircuitBreakerID | Text | CB3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2019
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | '327005139010001
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1
| Substation | Text | GSGR-039
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1
| Substation | Text | GSGR-039
| Type | Short Integer | 1 | 2
| FunctionType | Short Integer | 2 | 2
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2
| Substation | Text | GSGR-039
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2
| Substation | Text | GSGR-039
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 2 | 2
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3
| Substation | Text | GSGR-039
| Type | Short Integer | 1 | 1
| FunctionType | Short Integer | 1 | 1
| Manufacturer | Text | GE /Suzhou
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | Substation_Name | Short Integer | GISAGARA
| Substation_ID | Text | GSGR-039
| Substation_Total_Capacity_MVA | Double | 20
| Substation_Voltage_Level_kV | Short Integer | 13 | 13 | 220/30
| SubstationArrangement | Short Integer | 1 | 1
| Number_of_Power_Transformers | Short Integer | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 1
| Number_Distribution_Transf | Short Integer | 0
| Number of auxiliary transformers | Short Integer | 0 | 0 | This Should allow to add a Number of Aux TR not the chose Yes or Not
| Standby_Generators | Short Integer
| Busbar_Configuration_HV | Short Integer | 1 | 1
| Number of MV Feeders | Short Integer | 6
| Number of HV line Bays | Short Integer | 2
| Number of Trx Bays | Short Integer | 1
| Configuration_Busbar_MV | Short Integer | 1 | 1
| BuscouplerHV | Short Integer | 0 | 0
| BuscouplerMV | Short Integer | 0 | 0
| Type_of_Busbar_HV | Short Integer | 1 | 1
| Type_of_MV_switchgears | Short Integer | 1 | 1
| Year of Commissioning | Short Integer | 2020
| Year_of_upgrade | Short Integer
| Contractor_Name | Text | NCC
| Substation_Meter_SN | Text | Not Existing
| Lightning_protection | Short Integer | 1 | 1
| OperatorsLivingHouse | Short Integer | 0 | 0
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA1-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-1
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-2
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-3
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2020
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | 1 | 1
| Type_Surge_Arrester | Short Integer | 1 | 1
| Power_Frequency_Voltage_kV | Double | 550
| MaxContinuousOperatVolt_kV | Double | 102
| RatedVoltage_kV1 | Double | 110
| NominalDischargeCurrent_kA | Double | 20
| Rated_short_circuit_Current | Double | 31.5 |  | Unit in kA is missing
| Light_Impulse_Withsand_kV | Double | 1200
| PowerFrequencyWithstandVol | Double | 550 |  | Unit in kV is missing
| RatedContinuousContinuous_kv | Double | 102
| DischargeCounter | Short Integer | 1 | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | 2 | 2
| ProtClassDischargeCounter | Text | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | HBL
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| Type | Short Integer | 1 | 1
| Standards_ | Text | IEC 60623
| BatteryFloatingVoltage | Double | 50 |  | Unit in V is missing
| RatedVoltage | Double | 48 |  | Unit in V is missing
| TenHrsRatingCapacity | Double | 80 |  | Unit in Ah is missing
| One_min_rating_Current_A | Double | 800
| MaximumVolatge_V | Double | 55.2
| MinimumVoltage_V | Double | 40.8
| MinimumVoltageperCell | Double | 1.02
| NumberofCells | Short Integer | 40
| BatteryFloatingVoltage | Double | 53.9
| BoostChargingVoltage | Double | 55.8
| FloatChargeCurrent_A | Double | 6.2
| BoostChargeCurrent | Double | 60
| SelfDischargeat_25oC | Double | 0.7
| TypeofCooling | Text | Natural
| Charging time (hrs) | Double | 8
DC Supply 110 VDC Battery | Manufacturer | Text | HBL
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| Model | Text | 88 KBL
| Type | Short Integer | 1
| Standards_ | Text | IEC 60623
| RatedVoltage | Double | 110
| TenHrsRatingCapacity | Double | 255 |  | Unit in Ah is missing
| One_min_rating_Current_A | Double | 100
| MaximumVolatge_V | Double | 136.4
| MinimumVoltage_V | Double | 88
| MinimumVoltageperCell | Double | 1
| Number_of_cells__No_ | Long Integer | 88
| BatteryFloatingVoltage | Double | 126
| BoostChargingVoltage | Double | 123.3
| FloatChargeCurrent_A | Double | 6.2
| BoostChargeCurrent | Double | 100
| TypeofCooling | Short Integer | Natural
DC Supply 48 VDC charger | Manufacturer | Text | HBL power system Ltd
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| Model | Text
| Charger_type | Short Integer | 2 | 2
| Standards_ | Short Integer | DIN VDE 0558
| Frequency_Hz | Short Integer | 50 | 50
| AC_Supply_V_ | Double | 230
| Rated_InputPower_kVA | Double | 5.53
| DC Output (Kw) | Double | 2.88
| DC_Output_kV | Double | 48 |  | Unit in should be in V not in kV
| Rated_output_Voltage_V | Double | 48
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5
| OperatingConditions | Text
| Altitude_m | Double | 2000
| Degree_protection_ | Short Integer | 55 | 55
| DCDistributionBoard | Short Integer | 0 | 0
| RatedCurrent_A | Double
| NumberofFeeders | Short Integer
| short_circuit_capacity_breaker | Double
DC Supply 110 VDC charger | Manufacturer | Text | HBL power system Ltd
| Substation_ID | Text | GSGR-039
| CountryOfManufacturer | Text | INDIA
| Model | Text
| TypeofOperation | Short Integer | 1
| Charger_type | Short Integer | 2
| Standards_ | Text | DIN VDE 0558
| ChargingTime | Double | 5
| Frequency_Hz | Short Integer | 50
| AC_Supply_V_ | Double | 400
| Rated_InputPower_kVA | Double | 14.8
| VoltageVariation | Double |  |  | ±5% This should be a Text
| DC_Output_kV | Double | 110
| TypeofCharging | Text | Float/ Boost
| Rated_output_Voltage_V | Double | 110
| MaximumDC_Voltage_V | Double | 126
| ConstantVoltageAccuracy | Double |  |  | ±10% V This should be a Text
| Rated_DC_output_Current_A | Double | 130A
| FloatingVoltageRegulatin | Double | 104.4
| EqualisingVoltageRegulatin | Double | 128.8
| Minimum_Insulation_resistance_ | Double | 5
| TypeofCooling | Short Integer |  |  | Natural self-ventilating, Others (Domain code not given)
| Ambient_temperature | Double |  |  | This should be a Text 0°C to +40°C
| Altitude_m | Double | 1000
| Total_Weight_Charger_kg | Double | 340
| Degree_protection_ | Short Integer | 55
| RatedCurrent_A | Double | 100
| ShortCircuitStrength_kA_sec | Double
| BusbarMaterial | Short Integer |  |  | Copper tin-plate (No domain code is given)
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE
| Type | Text | REASON DR60
| Standards | Text | IEC61850
| Arrangement | Short Integer | 2 | 2
| VT_CT_Connection | Short Integer | 1 | 1
| Frequency_Hz | Short Integer | 50 | 50
| Nominal_input_current_A | Double | 1 |  | This can be programmed to accept 5A also
| Nominal_voltage_Vdc | Double | 110
| Power_consumption_VA | Double | 150
| NumberofAnalogInputs | Short Integer | 32
| NumberofBinaryInputs | Short Integer | 96
| NumberofBinaryOutputs | Short Integer | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | KIGOMA
| Year_of_commisioning | Short Integer | 2020
| ContractorName | Text | NCC
| Manufacturer | Text | Not known
| Voltage_Level_kV | Short Integer | 2 | 110
| CondustorSize | Short Integer | 6 | 6 | 240/40 Type has to Domain codes 3&6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 8.4
| CurrentCarryingCapacity | Double | 80 |  | Unit in MW is missing
| NominalBreakingLoad_KN | Double | 130
| MaxElectricResitance | Double | 0.119 |  | Unit in (Ώ/km)is missing
| PositiveSequenceReactance | Double | 0.427 |  | Unit in (Ώ/km)is missing
| PositiveSequenceResistance | Double | 0.123 |  | Unit in (Ώ/km)is missing
| ZeroSequenceResistance | Double | 0.327 |  | Unit in (Ώ/km)is missing
| ZeroSequenceReactance | Double | 1.119 |  | Unit in (Ώ/km)is missing
| ZeroSequenceCapacitance | Double | 0.011 |  | Unit in (Ώ/km)is missing
| PositiveSequenceCapacitance | Double | 0.0066 |  | Unit in (Ώ/km)is missing
High Voltage Line | Name | Text | NGOZI
| Year_of_commisioning | Short Integer | 2020
| ContractorName | Text | ELTEL
| Manufacturer | Text | Not known
| Voltage_Level_kV | Short Integer | 2 | 110
| CondustorSize | Short Integer | 6 | 6 | 240/40 Type has to Domain codes 3&6
| ShieldWire | Short Integer | 1 | 1
| ConductorType | Short Integer | 1 | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | 0 | 0
| Underground_Cable_Size | Short Integer
| UG_Length_Km | Double
| Length_of_the_Line_ | Double | 8.4
| CurrentCarryingCapacity | Double | 40 |  | Unit in MW is missing
| NominalBreakingLoad_KN | Double | 130
| MaxElectricResitance | Double | 0.119 |  | Unit in (Ώ/km)is missing
| PositiveSequenceReactance | Double | 0.427 |  | Unit in (Ώ/km)is missing
| PositiveSequenceResistance | Double | 0.123 |  | Unit in (Ώ/km)is missing
| ZeroSequenceResistance | Double | 0.327 |  | Unit in (Ώ/km)is missing
| ZeroSequenceReactance | Double | 1.119 |  | Unit in (Ώ/km)is missing
| ZeroSequenceCapacitance | Double | 0.011 |  | Unit in (Ώ/km)is missing
| PositiveSequenceCapacitance | Double | 0.0066 |  | Unit in (Ώ/km)is missing
Transformer Bay | Trx_Bay_ID | Text | D03
| Substation_ID | Text | GSGR-039
| Trx_Bay_Name | Text | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 2 | 2
| Trx_Bay_Capacity_MVA | Double | 20
| Frequency_Hz | Short Integer | 50 | 50
| Type_of_Trx_Differencial_relay | Text | ABB-RET670
| Type_of_Back_up_relay | Text | SIEMENS -7UT86
| Type_of_BCU_Bay_control_unit | Text | SIEMENS - 6MD85
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | SIEMENS
| CircuitBreakerID | Text | CB-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | 3HA49
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | 1 | 1
| ArcQuenchingMedium | Short Integer | 2 | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 15
| MaxContinuousOperatVolt_kV | Double | 24
| RatedImpulseWithstandVol | Double | 95
| PowerFrequencyWithstandVol | Double | 38
| Rated_Frequency | Short Integer | 50 | 50
| Rated_short_time_withstand_current__kA_ | Text | 25
| Rated_Peak_Short_Cir_Current | Double | 63
| RatedNormalCurrent_A | Double | 1250
| RatedShortCircuitBreakCur_kA | Double | 25
| RatedShortCircuitMakCurrent_A | Double | 63
| RatedCableChargingBreakingCur | Double | 50
| MaximumCApacitivBreakingCur | Double | 875
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60
| DeadTime_ms | Double | 300
| BreakTime_ms | Double | 85
| MakeTime_ms | Double | 70
| ArcingTime_ms | Double | 15
| AtRAtedContinuousCurrent | Double
| AtRAtedBreakingCurrent | Double
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110
| PowerSupply | Short Integer | 110
| HandOperatingFacility | Short Integer | 1 | 1
Indoor Current Transformer | Manufacturer | Text | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | 4MT74XD
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 30
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 500
| Rated_Secondary_Current | Double | 1
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 95kV
| LimitsContPrimaryCurrency_A | Double | 2400
Indoor Current Transformer | Manufacturer | Text | SIEMENS
| CurrentTransfomer_ID | Text | CT-MV3
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | 4MT74XD
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 30
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 300 |  | 300-150A (The CT has two Ratio and this should be a text )
| Rated_Secondary_Current | Double | 1 |  | Unit in A is missing
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10
| RatedShortTimeWithstandCur | Double | 25 |  | Unit in kA is missing
| Rated_Peak_Short_Cir_Current | Double | 63 |  | Unit in kA is missing
| RatedImpulseWithstandVol | Double | 170 |  | Unit in kV is missing
| LimitsContPrimaryCurrency_A | Double | 768
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV1
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70 |  | Unit in kV is missing
| RatedImpulseWithstandVol | Double | 170 |  | Unit in kV is missing
| RatedPrimaryVoltage_kV | Double | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 110
| Rated_secondary_voltage_winding_2__V_ | Text | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV2
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70
| RatedImpulseWithstandVol | Double | 170
| RatedPrimaryVoltage_kV | Double | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 110
| Rated_secondary_voltage_winding_2__V_ | Text | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 60
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | SIEMENS
| VoltageTransfomer_ID | Text | VT-MV3
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | 4MT74XD
| Rated_Frequency | Short Integer | 50 | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70 |  | Unit in kV is missing
| RatedImpulseWithstandVol | Double | 170 |  | Unit in kV is missing
| RatedPrimaryVoltage_kV | Double | 30
| Rated_secondary_voltage_winding_1__V_ | Text | 100
| Rated_secondary_voltage_winding_2__V_ | Text | 100
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 60
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-039
| Substation_ID | Text | GSGR-039
| Bay_ID | Text | D01
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5 |  | Unit in mm is missing
| Max_height_mm | Double | 2000
| MaxWidth_mm | Double | 1500
| MaxDepth | Double | 2500
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | ABB-RED670
Distance Protection | RelayType | Text | SIEMENS-7SA87
| Bay_ID | Text | D01
| Substatoin_ID | Text | GSGR-039
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1
| Rated_Voltage | Double | 100
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-039
| Substation_ID | Text | GSGR-039
| Bay_ID | Text | D02
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | 1 | 1
| FloorMounted | Short Integer | 1 | 1
| StainlessSteelSheetThickness | Double | 2.5
| Max_height_mm | Double | 2000
| MaxWidth_mm | Double | 1500
| MaxDepth | Double | 2500
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | ABB-RED670
Distance Protection | RelayType | Text | SIEMENS-7SA87
| Bay_ID | Text | D02
| Substatoin_ID | Text | GSGR-039
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1
| Rated_Voltage | Double | 100
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50 | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Standby Generator | Manufacturer | Text | CUMMINS POWER GENERATION
| Substation_ID | Text | GSGR-039
| Standby_Generator_ID | Text | DGU-1-039
| CountryOfManufacturer | Text | INDIA
| Mode_Operation | Short Integer
| Model | Text | C66D5L
| Type_Assembly | Short Integer
| Arrangement | Short Integer
| Phases | Short Integer | 3
| RatedOuptuPower_kVA | Double | 250
| RatedVoltage | Double | 400 |  | Unit in V is missing
| RatedCurrent_A | Double | 360
| PowerFactor | Double | 0.8
| CouplingofEngine | Text | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Cummins
| Governor | Text | PID
| GobernorBrand | Text
| RatedPower_kVA_kW | Double | 200
| CompressionRatio_ | Text | 15:01
| NoofCylinder | Short Integer | 6
| Speed_RPM | Double | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500
| Cooling_System | Short Integer | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 97
| LubricationOilConsumption | Double | 0.025 |  | Unit in l/h is missing
| Ambient_temperature | Double |  |  | Minus 20 0C up to Plus 40 0C (This should be a Text)
| Protection index | Text |  |  | IP44 (This should be a text)
| MethodofStarting | Text | Man/Auto
| Voltage_VDC | Double | 24
| Power_kW | Double | 200
| Battery_Capacity_Ah | Double | 135
| BatteryType | Text | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50
| VoltageRegulationMode | Short Integer |  |  | AVR (This should be a Text)
| Total_Weight | Double | 1453 |  | Unit in kg is missing