## KIGOMA SUBSTATION
KIGOMA
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-031
| PowerPlantID | Text | NA
| Substation_ID | Text | KGMA-031
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1
| Manufacturer | Text | ETRA
| CountryOfManufacturer | Text | SLOVENIA
| ManufacturerYear | Short Integer | 2008
| Year_commissioning | Short Integer | 2008
| Owner | Short Integer | REG |  | REG (This Should be a Text or create a Domain code)
| Rated_Power_MVA | Double | 10 MVA
| Primaryvoltage__kv | Double | 110 kV
| Secondaryvoltage__kv | Double | 30kV
| TertiaryCurrent_A | Short Integer | NA
| Nominal_Frequency | Short Integer | 50Hz
| PrimaryCurrent_A | Double | 52.5A
| SecondaryCurrent_A | Double | 192.6A
| TertiaryCurrent_A | Double | NA |  | No Domain Code is proposed
| Vector_Group_Trx | Short Integer | YNyn0+d11
| CoolingMethod | Short Integer | ONAN
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR
| PercentageImpedance | Double | 6%
| NoLoadCurr_Percentage | Double | 10%
| Winding_Material | Short Integer | Copper
| Number_windings | Short Integer | 2
| No_Load_losses | Double | 20kW
| LoadLosses | Double | 90kW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 75dB
| NumberOfTappingPosition | Short Integer | 17
| TapChangerType | Short Integer | On-load
| TapChangerModel | Text | MS III300Y/123B/10193G
| TappingRange | Double | 110±16% |  | REG (This Should be a Text or create a Domain code)
| Tap_changer_manufacturer | Text | MR
| Tap_changer_country_orgin_ | Text | GERMANY
| TapChangerManufacturingDate | Short Integer | 2008
| SerialNumber | Text | 587415
| Barcode | Text | NA
| TotalWeight | Double | 34000kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 8900kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double | Not provided
| Depth | Double | Not provided
| Width | Double | Not provided
| Bushing_Material | Short Integer | Porcelain
Earthing Transformer | transfomerID | Text | AUX-TR1-031
| PowerPlantID | Text | NA
| Substation_ID | Text | KGMA-031
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1
| Manufacturer | Text | UNELEC FRANCE
| CountryOfManufacturer | Text | FRANCE
| ManufacturerYear | Short Integer | 1974
| Owner | Short Integer | REG
| Primaryvoltage__kv | Double | 30kV
| Secondaryvoltage__kv | Double | 0.4kV
| TertiaryCurrent_A | Short Integer | Not Exising
| Nominal_Frequency | Short Integer | 50Hz
| PrimaryCurrent_A | Double | 1.92A
| SecondaryCurrent_A | Double | 145A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | Yzn5
| CoolingMethod | Short Integer | ONAN
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | Unknown,
| PercentageImpedance | Double | 4%
| No_Load_losses | Double | 2kW
| LoadLosses | Double | 0.5KW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 55dB
| NumberOfTappingPosition | Short Integer | 3
| Standard_Code | Text | IEC 60076-7
| Tap_changer | Short Integer | OFF LOAD
| VoltageVariationRange1 | text | 30±2.5%
| Tap_changer_manufacturer | Text | UNELEC FRANCE
| Tap_changer_country_orgin_ | Text | FRANCE
| TapChangerManufacturingDate | Short Integer | 1974
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text | NA
| TotalWeight | Double | 865kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 246kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| WeightOfAccessories | Double | Not provided
| LV_CB_A | Short Integer | 400A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 1974
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | KGMA-031
| Busbar_HV_ID | Text | BB-031
| Number_of_Busbar_HV | Short Integer | 1
| Number_of_Busbar_MV | Short Integer | 2
| Type_of_Busbar | Short Integer | String Conductor ACSR 240/40mm2
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | ACSR | 1
| Barcode | Short Integer | NA
| Operating_Voltage_Level_kV | Double | 110kV
| Short_circuit_current_kA | Double | 40kA
| Nominal_Current_A | Double | 454A
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H01
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VBG07028819/2001
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H02
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 1
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VBG07028819/2002
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H03
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VBG07028819/2003
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H04
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VBG07028819/2004
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H05
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VBG07028819/2006
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
MV Switch gear | SwitchGearID | Text | SWG-001
| Substation_ID | Text | KGMA-031
| FeederID | Text | H06
| FeederName | Text | INCOMER TR1
| PanelFunction | Short Integer | Incomer feeder | 2
| SwitchingDevices | Short Integer | CB with isolator | 1
| Type_of_MV_cable_termination | Short Integer | I-Type | 1
| Insulation_Medium | Short Integer | SF6 | 1
| Manufacturing_Year | Short Integer | 2004
| Serial_Number | Text | 1VB2117021
| Manufacturer | Text | ABB
| Year_of_Commissioning | Short Integer | 2004
| Country_origin | Text | GERMANY
| Type_Model | Text | ZX2
| Altitude_m | Double | 2000m
| Nominal_voltage_kV | Double | 30KV
| Standards | Text | 60870-5-103
| Frequency_Hz | Short Integer | 50Hz | 50
| Rated_voltage_kV | Double | 30kV
| Maximum_continu_system_voltage | Double | 36kV
| type_protection_relay | Short Integer | REF 542plus | REF 542plus
| Rated_short_circuit_current | Double | 25kA
| Ratedpeak_shortcircuitcurrent | Double | 63kA
| RatedBusbar_Current | Double | 1250A
| Rated_SF6_Pressure_Kpa | Double | 130kPa
| Minimum_functional_level_for_SF6__KPa_ | Double | 100kPa
| Smart_meter_Installed | Short Integer | No | 0
| Meter_number___if_yes_ | Text | Not existing
Line Bay | Line_Bay_ID | Text | E01
| Substation_ID | Text | KGMA-031
| Line_Bay_Name | Text | MONT KIGALI
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 542plus
Line Bay | Line_Bay_ID | Text | E02
| Substation_ID | Text | KGMA-031
| Line_Bay_Name | Text | KILINDA
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | SIEMENS-7SD522
| Type_of_Distance_relay | Text | Including in 7SD522
| Type_of_Back_up_relay | Text | Including in 7SD522
| Type_of_BCU_Bay_control_unit | Text | ABB-REF 542plus
Line Bay | Line_Bay_ID | Text | E04
| Substation_ID | Text | KGMA-031
| Line_Bay_Name | Text | GISAGARA
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 6
| Line_Bay_Capacity_MVA | Double | 40MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | ABB-RED670
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | Including in RED 670
| Type_of_BCU_Bay_control_unit | Text | SIEMENS-6MD85
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-1
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-2
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT1-3
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-1
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | MEHRU
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-2
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | MEHRU
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT4-3
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | MEHRU
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2021
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-1
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-2
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-3
| Substation_ID | Text | KGMA-031
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 123kV
| TypeofVoltageTransformer | Short Integer | Induvtive | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 200VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,5 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT1-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y907
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT1-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y909
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT1-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y905
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT2-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y904
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT2-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y908
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | JIANGSU DAGO CHINA
| Current Transfomer ID | Text | CT2-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Double | 2009
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 5A
| Burden_VA | Double | 40VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 2009Y906
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | MEHRU
| Current Transfomer ID | Text | CT3-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | OC 8344/3/1/21
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | MEHRU
| Current Transfomer ID | Text | CT3-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | OC 8344/3/2/21
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | MEHRU
| Current Transfomer ID | Text | CT3-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Double | 2021
| Standard_Code | Text | IEC 185-1987
| RatedOutput_VA | Double | 40VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.5-5P20
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | OC 8344/3/3/21
| SF_ALF | Text | 5_20
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | JIANGSU DAGO CHINA
| CircuitBreakerID | Text | CB1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 2009Y905/2009Y906/2009Y910
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 126kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1543kg
| TotalMassofInsulatingMed | Double | 10kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | JIANGSU DAGO CHINA
| CircuitBreakerID | Text | CB2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 2009Y905/2009Y906/2009Y910
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 126kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1543kg
| TotalMassofInsulatingMed | Double | 10kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | JIANGSU DAGO CHINA
| CircuitBreakerID | Text | CB3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 6834-21-2032913/1
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 126kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.6 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1543kg
| TotalMassofInsulatingMed | Double | 10kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE Suzhou China
| CircuitBreakerID | Text | CB4
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2019
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | "3271005139003000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 145kV
| HighestSystemVoltage_kV | Double | 170kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3s
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50A
| RatedShortCircuitMakCurrent_A | Double | 100kA
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64 Mpa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50ms
| MaximumMakingTime_ms | Double | 70ms
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double | -30°C/+50°C
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000m
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Local (Handle), Remote ( Relay), Spring, Manual, Local (Handle) - Remote ( Relay) - Spring - Manual, Others | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1423.3kg
| TotalMassofInsulatingMed | Double | 8.3kg
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-1
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-1
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 1
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | YES | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-2
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 1
| Manufacturer | Text | JIANGSU DAGO
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2009
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-3
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | AREVA
| CountryOfManufacturer | Text | ITALY
| ManufacturerYear | Short Integer | 2007
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-4
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | GE Suzhou China
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-4
| Substation | Text | KGMA-031
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Line | 1
| Manufacturer | Text | GE Suzhou China
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2020
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | Substation_Name | Short Integer | KIGOMA
| Substation_ID | Text | KGMA-031
| Substation_Total_Capacity_MVA | Double | 10MVA
| Substation_Voltage_Level_kV | Short Integer | 110/15kV | 9
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 1
| Numbe_of_Earthing_Transfomer | Short Integer | 0
| Number_Distribution_Transf | Short Integer | 0
| Number of auxiliary transformers | Short Integer | 1 | 1
| Standby_Generators | Short Integer | YES
| Busbar_Configuration_HV | Short Integer | Single Busbar | 2
| Number of MV Feeders | Short Integer | 6
| Number of HV line Bays | Short Integer | 3
| Number of Trx Bays | Short Integer | 1
| Configuration_Busbar_MV | Short Integer | Single busbar | 2
| BuscouplerHV | Short Integer | No | 1
| BuscouplerMV | Short Integer | No | 1
| Type_of_Busbar_HV | Short Integer | Conductor | 2
| Type_of_MV_switchgears | Short Integer | Gas Insulated | 1
| Year of Commissioning | Short Integer | 1974
| Year_of_upgrade | Short Integer | 1987 & 2009
| Contractor_Name | Text | SGEEM-GTME-AEPE
| Substation_Meter_SN | Text | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 1
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA1-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B335
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA1-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B337
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA1-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B333
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA2-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B341
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA2-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B3426
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA2-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B329
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA3-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B340
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA3-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B339
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | JIANGSU DAGO CHINA
| ArresterID | Text | SA3-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2009
| SerialNumber | Text | 2009B38
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | JIANGSU DAGO CHINA
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | Y10W-102/266W1GT
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-1
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2021
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-2
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2021
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-3
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2021
| SerialNumber | Text | Not accesible (Require shutdown)
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 230kV
| MaxContinuousOperatVolt_kV | Double | 102kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 20kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| RatedContinuousContinuous_kv | Double | 102kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | HOPPECKE
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V
| RatedVoltage | Double | 48V
| TenHrsRatingCapacity | Double | 60Ah
| One_min_rating_Current_A | Double | 120A
| MaximumVolatge_V | Double | 48+15%
| MinimumVoltage_V | Double | 48-15%
| MinimumVoltageperCell | Double | 1.2V
| NumberofCells | Short Integer | 40
| BatteryFloatingVoltage | Double | 50
| BoostChargingVoltage | Double | 55.8V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 60A
| SelfDischargeat_25oC | Double | 7%
| TypeofCooling | Text | Natural
| Charging time (hrs) | Double | 5hrs
DC Supply 110 VDC Battery | Manufacturer | Text | GAZ
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| Model | Text | KL 200P
| Type | Short Integer | NiCd
| Standards_ | Text | DIN 41772
| RatedVoltage | Double | 110V
| TenHrsRatingCapacity | Double | 200Ah
| One_min_rating_Current_A | Double | 300A
| MaximumVolatge_V | Double | 110+15%
| MinimumVoltage_V | Double | 110-15%
| MinimumVoltageperCell | Double | 1.02V
| Number_of_cells__No_ | Long Integer | 90
| BatteryFloatingVoltage | Double | 112.5V
| BoostChargingVoltage | Double | 132.3V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 200A
| TypeofCooling | Short Integer | Natural
DC Supply 48 VDC charger | Manufacturer | Text | AEG GmbH
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | GERMANY
| Model | Text | Profitec 2000 S 48V/60A
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 5.53kVA
| DC Output (Kw) | Double | 2.88kW
| DC_Output_kV | Double | 48V
| Rated_output_Voltage_V | Double | 48V
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ
| OperatingConditions | Text
| Altitude_m | Double | 2000m
| Degree_protection_ | Short Integer | IP 20 | 55
| DCDistributionBoard | Short Integer | No | 0
| RatedCurrent_A | Double | NA
| NumberofFeeders | Short Integer | NA
| short_circuit_capacity_breaker | Double | NA
DC Supply 110 VDC charger | Manufacturer | Text | EDITELEKITRONIK
| Substation_ID | Text | KGMA-031
| CountryOfManufacturer | Text | TURKEY
| Model | Text | ERD-3P/110/100A
| TypeofOperation | Short Integer | Parallel
| Charger_type | Short Integer | Thyristor controlled
| Standards_ | Text | DIN VDE 0558
| ChargingTime | Double | 5h
| Frequency_Hz | Short Integer | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 17.3kVA
| VoltageVariation | Double | ±5%
| DC_Output_kV | Double | 110V
| TypeofCharging | Text | Float/ Boost
| Rated_output_Voltage_V | Double | 110V
| MaximumDC_Voltage_V | Double | 126V
| ConstantVoltageAccuracy | Double | ±10%
| Rated_DC_output_Current_A | Double | 100A
| FloatingVoltageRegulatin | Double | 104.4V
| EqualisingVoltageRegulatin | Double | 128.8V
| Minimum_Insulation_resistance_ | Double | 5MΏ
| TypeofCooling | Short Integer | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C
| Altitude_m | Double | >1000m
| Total_Weight_Charger_kg | Double | 340kg
| Degree_protection_ | Short Integer | IP20
| RatedCurrent_A | Double | 100A
| ShortCircuitStrength_kA_sec | Double | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate, Others
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE
| Type | Text | REASON DR60
| Standards | Text | IEC61850
| Arrangement | Short Integer | Panel mounted | 2
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A
| Nominal_voltage_Vdc | Double | 110DC
| Power_consumption_VA | Double | 150VA
| NumberofAnalogInputs | Short Integer | 32
| NumberofBinaryInputs | Short Integer | 96
| NumberofBinaryOutputs | Short Integer | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MONT KIGALI
| Year_of_commisioning | Short Integer | 1974
| ContractorName | Text | SGEEM
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 40.4km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 130kN
| MaxElectricResitance | Double | 0.119(Ώ/km)
| PositiveSequenceReactance | Double | 0.427(Ω/km)
| PositiveSequenceResistance | Double | 0.123(Ω/km)
| ZeroSequenceResistance | Double | 0.327(Ω/km)
| ZeroSequenceReactance | Double | 1.119(Ω/km)
| ZeroSequenceCapacitance | Double | 0.011(µf/km)
| PositiveSequenceCapacitance | Double | 0.0066(µF/km)
High Voltage Line | Name | Text | KILINDA
| Year_of_commisioning | Short Integer | 1974
| ContractorName | Text | SGEEM
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 110kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR,CU | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 27.5km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 130kN
| MaxElectricResitance | Double | 0.119(Ώ/km)
| PositiveSequenceReactance | Double | 0.427(Ω/km)
| PositiveSequenceResistance | Double | 0.123(Ω/km)
| ZeroSequenceResistance | Double | 0.327(Ω/km)
| ZeroSequenceReactance | Double | 1.119(Ω/km)
| ZeroSequenceCapacitance | Double | 0.011(µf/km)
| PositiveSequenceCapacitance | Double | 0.0066(µF/km)
Transformer Bay | Trx_Bay_ID | Text | E03
| Substation_ID | Text | KGMA-031
| Trx_Bay_Name | Text | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 10MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | SCHNEIDER - MICOM P632
| Type_of_Back_up_relay | Text | Included in MICOM P632
| Type_of_BCU_Bay_control_unit | Text | ABB - REF542+
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB
| CircuitBreakerID | Text | CB-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | VD4X3612-25
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 1250A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | ABB
| CircuitBreakerID | Text | CB-MV3
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | VD4X3612-25
| Standard | Text | IEC 62271-200
| CombinedEArthBusbarDisc | Short Integer | YES | 1
| ArcQuenchingMedium | Short Integer | Vacuum | 2
| Number_phases | Long Integer | 3
| RatedVoltage_kV1 | Double | 30kV
| MaxContinuousOperatVolt_kV | Double | 36kV
| RatedImpulseWithstandVol | Double | 170kV
| PowerFrequencyWithstandVol | Double | 70kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Rated_short_time_withstand_current__kA_ | Text | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedNormalCurrent_A | Double | 1250A
| RatedShortCircuitBreakCur_kA | Double | 25kA
| RatedShortCircuitMakCurrent_A | Double | 63kA
| RatedCableChargingBreakingCur | Double | 50A
| MaximumCApacitivBreakingCur | Double | 875A
| Rated_Operating_Sequence | Text | O-0.3S-CO-3MIN-CO
| ClosingTime_ms | Double | 60ms
| DeadTime_ms | Double | 300ms
| BreakTime_ms | Double | 85ms
| MakeTime_ms | Double | 70ms
| ArcingTime_ms | Double | 15ms
| AtRAtedContinuousCurrent | Double | Not existing
| AtRAtedBreakingCurrent | Double | Not existing
| NumberofNO | Short Integer | 8
| NumberofNc | Short Integer | 8
| RatedMotorVoltage_VDC | Double | 110V
| NumberofMakingCoils | Short Integer | 1
| NumberofTrippingCoils | Short Integer | 1
| Volatge_VDC | Double | 110V
| PowerSupply | Short Integer | 110V DC
| HandOperatingFacility | Short Integer | Yes | 1
Indoor Current Transformer | Manufacturer | Text | WTW
| CurrentTransfomer_ID | Text | CT-MV1
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | EVEG-36-34
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1-1A
| AccuracyClass | Text | Cl 0.5-5P20
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV |  |  | 313.4796
| LimitsContPrimaryCurrency_A | Double | 120%
Indoor Current Transformer | Manufacturer | Text | WTW
| CurrentTransfomer_ID | Text | CT-MV3
| CountryOfManufacturer | Text | GERMANY
| Type__model | Text | ASG-36-5
| Standard | Text | IEC 61869-1
| RatedVoltage_kV1 | Double | 36kV
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| NumberofCores | Short Integer | 3
| Rated_Primary_Current_A | Double | 80-240-640A
| Rated_Secondary_Current | Double | 150mV
| AccuracyClass | Text | Cl 1
| Burden_VA | Double | 10VA
| RatedShortTimeWithstandCur | Double | 25kA
| Rated_Peak_Short_Cir_Current | Double | 63kA
| RatedImpulseWithstandVol | Double | 170kV
| LimitsContPrimaryCurrency_A | Double | NA
Indoor Voltage Transformer | Manufacturer | Text | WTW
| VoltageTransfomer_ID | Text | VT-MV1
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | EVEG-36-0.5
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV
| RatedImpulseWithstandVol | Double | 170kV
| RatedPrimaryVoltage_kV | Double | 30kV
| Rated_secondary_voltage_winding_1__V_ | Text | 100V
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 15VA
| TertiaryVoltage_kV | Long Integer
Indoor Voltage Transformer | Manufacturer | Text | WTW
| VoltageTransfomer_ID | Text | VT-MV3
| CountryOfManufacturer | Text | GERMANY
| Standard | Text | IEC 61869-1
| TypeofVoltageTransformer | Short Integer | EVEG-36-0.5
| Rated_Frequency | Short Integer | 50Hz | 50
| Number_phases | Long Integer | 1
| PowerFrequencyWithstandVol | Double | 70kV
| RatedImpulseWithstandVol | Double | 170kV
| RatedPrimaryVoltage_kV | Double | 30kV
| Rated_secondary_voltage_winding_1__V_ | Text | 100V
| Rated_secondary_voltage_winding_2__V_ | Text | 100V/3
| Accuracy_class__measuring_ | Text | Cl 0.2 FS5
| Accuracy_class__protection_ | Text | Cl 3P
| RatedOutput_VA | Double | 15VA
| TertiaryVoltage_kV | Long Integer
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-1-001
| Substation_ID | Text | KGMA-031
| Bay_ID | Text | E01
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | KGMA-031
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | 2010
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | RS 485
Control and Protection Panels | Standards | Text | Feeder Adaptation Unit
| Control_Protection_Panel_ID | Text | TSP-CPR-2-001
| Substation_ID | Text | KGMA-031
| Bay_ID | Text | E02
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | SIEMENS-7SD522
Distance Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E02
| Substatoin_ID | Text | KGMA-031
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | 2010
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Transformer Protection | RelayType | Text | SCHNEIDER - MICOM P632
| Bay_ID | Text | E03
| Substatoin_ID | Text | KGMA-031
| Manufacturer | Text | SCHNEIDER
| Country_manufacturer_ | Text | ENGLAND
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E01
| Substatoin_ID | Text | KGMA-031
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | Included in SIEMENS-7SD522
| Bay_ID | Text | E02
| Substatoin_ID | Text | KGMA-031
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Standby Generator | Manufacturer | Text | Not Existing
| Substation_ID | Text | Not Existing
| Standby_Generator_ID | Text | Not Existing
| CountryOfManufacturer | Text | Not Existing
| Mode_Operation | Short Integer | Not Existing
| Model | Text | Not Existing
| Type_Assembly | Short Integer | Not Existing
| Arrangement | Short Integer | Not Existing
| Phases | Short Integer | Not Existing
| RatedOuptuPower_kVA | Double | Not Existing
| RatedVoltage | Double | Not Existing
| RatedCurrent_A | Double | Not Existing
| PowerFactor | Double | Not Existing
| CouplingofEngine | Text | Not Existing
| FuelLevelEmissionPerm | Double | Not Existing
| DieselEngineType | Text | Not Existing
| Governor | Text | Not Existing
| GobernorBrand | Text | Not Existing
| RatedPower_kVA_kW | Double | Not Existing
| CompressionRatio_ | Text | Not Existing
| NoofCylinder | Short Integer | Not Existing
| Speed_RPM | Double | Not Existing
| Applicable_Standard | Text | Not Existing
| SpeedREgulation | Short Integer | Not Existing
| Fuel_Tank_Capacity | Double | Not Existing
| Cooling_System | Short Integer | Not Existing
| NoiseatFullLoad | Double | Not Existing
| LubricationOilConsumption | Double | Not Existing
| Ambient_temperature | Double | Not Existing
| Protection index | Text | Not Existing
| MethodofStarting | Text | Not Existing
| Voltage_VDC | Double | Not Existing
| Power_kW | Double | Not Existing
| Battery_Capacity_Ah | Double | Not Existing
| BatteryType | Text | Not Existing
| BrandandModelofBattery | Text | Not Existing
| Frequency_Hz | Short Integer | Not Existing | 50
| VoltageRegulationMode | Short Integer | Not Existing
| Total_Weight | Double | Not Existing