## RWABUSORO SUBSTATION
RWABUSORO
Device | Field | Data Type | Domain | Domain Code
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-1-038
| PowerPlantID | Text | NA
| Substation_ID | Text | RBSR-038
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | CHINT
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2019
| Year_commissioning | Short Integer | 2019
| Owner | Short Integer | REG
| Rated_Power_MVA | Double | 93.8MVA
| Primaryvoltage__kv | Double | 220 kV
| Secondaryvoltage__kv | Double | 110kV
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 246.4A
| SecondaryCurrent_A | Double | 493.4A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | YN0d11 | 17
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 9.5%
| NoLoadCurr_Percentage | Double | 10%
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2
| No_Load_losses | Double | 65kW
| LoadLosses | Double | 470kW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 75dB
| NumberOfTappingPosition | Short Integer | 25
| TapChangerType | Short Integer | On-load | 1
| TapChangerModel | Text | 3×VMI501-170/C-14273W
| TappingRange | Double | 220±16%
| Tap_changer_manufacturer | Text | MR
| Tap_changer_country_orgin_ | Text | GERMANY
| TapChangerManufacturingDate | Short Integer | 2019
| SerialNumber | Text | 2120048
| Barcode | Text | NA
| TotalWeight | Double | 125100kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 37500kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double | Not provided
| Depth | Double | Not provided
| Width | Double | Not provided
| Bushing_Material | Short Integer | Porcelain | 1
Power Transformer/ Stepup Transformer | transfomerID | Text | PTR-2-038
| PowerPlantID | Text | NA
| Substation_ID | Text | RBSR-038
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR2 | 1
| Manufacturer | Text | SAN BIAN
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2023
| Year_commissioning | Short Integer | 2023
| Owner | Short Integer | REG
| Rated_Power_MVA | Double | 25MVA
| Primaryvoltage__kv | Double | 220 kV
| Secondaryvoltage__kv | Double | 30kV
| TertiaryCurrent_A | Short Integer | NA | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 65.6A
| SecondaryCurrent_A | Double | 481.6A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | YNd11 | 17
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR | 1
| PercentageImpedance | Double | 10.19%
| NoLoadCurr_Percentage | Double | 10%
| Winding_Material | Short Integer | Copper | 1
| Number_windings | Short Integer | 2
| No_Load_losses | Double | 17.5kW
| LoadLosses | Double | 125kW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 75dB
| NumberOfTappingPosition | Short Integer | 5
| TapChangerType | Short Integer | Off-load | 1
| TapChangerModel | Text | W(DDD) BII 400/252-6.5(511)
| TappingRange | Double | 110±16%
| Tap_changer_manufacturer | Text | Wuhan Taipu Ltd
| Tap_changer_country_orgin_ | Text | CHINA
| TapChangerManufacturingDate | Short Integer | 2023
| SerialNumber | Text | 2301G105-1-2-3
| Barcode | Text | NA
| TotalWeight | Double | 67660kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 18350kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| Height | Double | Not provided
| Depth | Double | Not provided
| Width | Double | Not provided
| Bushing_Material | Short Integer | Porcelain | 1
Earthing Transformer | transfomerID | Text | AUX-TR1-038
| PowerPlantID | Text | NA
| Substation_ID | Text | RBSR-038
| PowerPlantname | Text | NA
| TransformerNaming | Short Integer | TR1 | 0
| Manufacturer | Text | CHINT
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Short Integer | 2019
| Owner | Short Integer | REG | 1
| Primaryvoltage__kv | Double | 11kV
| Secondaryvoltage__kv | Double | 0.4kV
| TertiaryCurrent_A | Short Integer | Not Exising | 0
| Nominal_Frequency | Short Integer | 50Hz | 50
| PrimaryCurrent_A | Double | 16.5A
| SecondaryCurrent_A | Double | 455.2A
| TertiaryCurrent_A | Double | NA
| Vector_Group_Trx | Short Integer | Dyn11 | 20
| CoolingMethod | Short Integer | ONAN | 1
| Phases | Short Integer | 3
| WorkingCondition | Short Integer | OUTDOOR | 0
| PercentageImpedance | Double | 4%
| No_Load_losses | Double | 0.4kW
| LoadLosses | Double | 5.2KW
| AltitudeLevel | Double | 2000m
| Noiselevel_db | Double | 55dB
| NumberOfTappingPosition | Short Integer | 3
| Standard_Code | Text | IEC 60076
| Tap_changer | Short Integer | OFF LOAD
| VoltageVariationRange1 | text | 15±2.5%
| Tap_changer_manufacturer | Text | FRANCE TRANSFO
| Tap_changer_country_orgin_ | Text | FRANCE
| TapChangerManufacturingDate | Short Integer | 1987
| SerialNumber | Text | Incorporated in Transformer
| Barcode | Text | NA
| TotalWeight | Double | 1140kg
| WeightOfActivePart | Double | Not provided
| WeightOfOil | Double | 215kg
| WeightOfUpperTank | Double | Not provided
| TransportationOfWeight_N2 | Double | Not provided
| WeightOfAccessories | Double | Not provided
| LV_CB_A | Short Integer | 630A
| Earthing_Switch | Short Integer | NA
| Notes | Text | NA
| Branch | text | NA
| Year_commissioning | Short Integer | 1987
High Voltage Busbar/Medium Voltage Busbar | Substation_ID | Text | RBSR-038
| Busbar_HV_ID | Text | BB-038
| Number_of_Busbar_HV | Short Integer | 2
| Number_of_Busbar_MV | Short Integer | 0
| Type_of_Busbar | Short Integer | Tubular
| Phase_sequence | Short Integer | ABC | 7
| Busbar_Material | Short Integer | Aluminium | 3
| Barcode | Short Integer | NA
| Operating_Voltage_Level_kV | Double | 220kV
| Short_circuit_current_kA | Double | 50kA
| Nominal_Current_A | Double | 960A
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_busbar_protection_relay_differential | Text | Not Existing
MV Switch gear | SwitchGearID | Text | Not Existing
| Substation_ID | Text | Not Existing
| FeederID | Text | Not Existing
| FeederName | Text | Not Existing
| PanelFunction | Short Integer | Not Existing | 4
| SwitchingDevices | Short Integer | Not Existing | 3
| Type_of_MV_cable_termination | Short Integer | Not Existing | 0
| Insulation_Medium | Short Integer | Not Existing | 1
| Manufacturing_Year | Short Integer | Not Existing
| Serial_Number | Text | Not Existing
| Manufacturer | Text | Not Existing
| Year_of_Commissioning | Short Integer | Not Existing
| Country_origin | Text | Not Existing
| Type_Model | Text | Not Existing
| Altitude_m | Double | Not Existing
| Nominal_voltage_kV | Double | Not Existing
| Standards | Text | Not Existing
| Frequency_Hz | Short Integer | Not Existing | 50
| Rated_voltage_kV | Double | Not Existing
| Maximum_continu_system_voltage | Double | Not Existing
| type_protection_relay | Short Integer | Not Existing | REF 542plus
| Rated_short_circuit_current | Double | Not Existing
| Ratedpeak_shortcircuitcurrent | Double | Not Existing
| RatedBusbar_Current | Double | Not Existing
| Rated_SF6_Pressure_Kpa | Double | Not Existing
| Minimum_functional_level_for_SF6__KPa_ | Double | Not Existing
| Smart_meter_Installed | Short Integer | Not Existing | 0
| Meter_number___if_yes_ | Text | Not Existing
Line Bay | Line_Bay_ID | Text | D01
| Substation_ID | Text | RBSR-038
| Line_Bay_Name | Text | MAMBA 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6
| Line_Bay_Capacity_MVA | Double | 80MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | D02
| Substation_ID | Text | RBSR-038
| Line_Bay_Name | Text | MAMBA 2
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6
| Line_Bay_Capacity_MVA | Double | 80MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | D05
| Substation_ID | Text | RBSR-038
| Line_Bay_Name | Text | KIGOMA 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6
| Line_Bay_Capacity_MVA | Double | 80MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | D06
| Substation_ID | Text | RBSR-038
| Line_Bay_Name | Text | BUGESERA 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6
| Line_Bay_Capacity_MVA | Double | 80MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500
Line Bay | Line_Bay_ID | Text | D07
| Substation_ID | Text | RBSR-038
| Line_Bay_Name | Text | BUGESERA 2
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 6
| Line_Bay_Capacity_MVA | Double | 80MW
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Line_Diffe_relay | Text | EFACEC-TPU D500
| Type_of_Distance_relay | Text | SIEMENS-7SA87
| Type_of_Back_up_relay | Text | EFACEC-TPU S430
| Type_of_BCU_Bay_control_unit | Text | EFACEC-BCU500
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT2-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT3-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT5-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT6-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT7-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT9-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT91-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT91-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT91-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT10-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT11-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 950kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT20-1
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT20-2
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Voltage Transformer | VoltageTransfomer_ID | Text | VT20-3
| Substation_ID | Text | RBSR-038
| Manufacturer | Text | GE T&D India LTD
| CountryOfManufacturer | Text | India
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 60044-5/2004
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| TypeofVoltageTransformer | Short Integer | Capacitator | 1
| AltitudeLevel | Double | 2000m
| Winding_Material | Short Integer | Copper | 1
| RatedOutput_VA | Double | 100VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | 0.1kV
| AccuracyClass | Text | Cl.0,2 & Cl.3P
| MaxThermalOutput | Double | 1000 VA
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Double | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | 1.2cont./1.5 for 30s
| Light_Impulse_Withsand_kV | Double | 550kV
| Degree_of_Protection | Text | IP55
| Insulation_ | Short Integer | Oil | 1
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT1-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 1000-2000A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023682
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT1-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 1000-2000A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023680
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT1-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 1000-2000A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023681
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT2-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 379940697
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT2-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 379940696
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT2-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 379940695
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT3-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023700
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT3-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023699
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT3-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023698
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT4-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023658
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT4-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023657
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT4-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023656
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT5-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023688
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT5-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023579
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT5-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023580
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT6-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023691
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT6-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023690
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT6-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023689
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT7-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023694
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT7-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023693
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT7-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 400-800A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023692
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | ARTECHE
| Current Transfomer ID | Text | CT8-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | China
| ManufacturerYear | Double | 2022
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 22006017/1
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | ARTECHE
| Current Transfomer ID | Text | CT8-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | China
| ManufacturerYear | Double | 2022
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 22006017/3
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | ARTECHE
| Current Transfomer ID | Text | CT8-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | China
| ManufacturerYear | Double | 2022
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 200-400A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 22006017/2
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT9-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023477
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT9-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023476
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT9-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37904023475
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT91-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023745
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT91-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 110kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994026875
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
Current Transformer | Manufacturer | Text | GE T&D
| Current Transfomer ID | Text | CT91-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | India
| ManufacturerYear | Double | 2018
| Standard_Code | Text | IEC 60044-1/03
| RatedOutput_VA | Double | 30VA
| Primaryvoltage__kv | Double | 220kV
| Secondaryvoltage__kv | Double | NA
| AccuracyClass | Text | Cl 0.2-5P10
| MaxThermalOutput | Double | 120%
| InsulationLV_kV | Double | 1kV
| Frequency_Hz | Short Integer | 50Hz | 50
| TemperatureRange | Double | -25°C/+40°C
| RatedVoltageFactor | Double | NA
| NumberofCores | Short Integer | 2
| Rated_Primary_Current_A | Double | 600-1200A
| Rated_Secondary_Current | Double | 1A
| Burden_VA | Double | 30VA
| RatedShortTime_CirCurrent_kA | Double | 31.5kA
| Rated_Peak_Short_Cir_Current | Double | 80kA
| KneePoint_V | Double | NA
| SerialNumber | Text | 37994023743
| SF_ALF | Text | 5_10
| LimitsContPrimaryCurrency_A | Double | 120%
| PowerFrequencyTestVoltage_kV | Double | 230kV
| Insulator | Short Integer | Oil, Others | 1
| Degree_of_Protection | Text | Porcelain
| RatedContThermCurrentFactor_A | Double | 120%
| DurationofShortCircuit_s | Double | 3s
| AltitudeLevel | Double | 2000m
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | '32710047900020005
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 1
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900010000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 1
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900010000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB4
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 2710047900020000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB5
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900010000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB6
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900010000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB7
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900010000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB8
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 3620270030002
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 220kV
| HighestSystemVoltage_kV | Double | 245kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 1200kV
| PowerFrequencyWithstandVol | Double | 530kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.64MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer
| TotalMassCircuitbreaker_kg | Double | 3230kg
| TotalMassofInsulatingMed | Double | 30.8kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB9
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900030000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Three Pole | 3
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.74MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1534kg
| TotalMassofInsulatingMed | Double | 10kg
High Voltage Circuit Breaker/High Voltage Circuit Breaker | Manufacturer | Text | GE t&D india LTD
| CircuitBreakerID | Text | CB91
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-100
| SerialNumber | Text | 32710047900030000
| Insulation_medium | Short Integer | SF6 | 1
| Class | Text | Class A
| CommandModel | Short Integer | Single Pole | 3
| RatedVoltage_kV1 | Double | 110kV
| HighestSystemVoltage_kV | Double | 145kV
| Rated_Frequency | Short Integer | 50Hz
| Nominal_Current_A | Double | 3150A
| RatedImpulseWithstandVol | Double | 650kV
| PowerFrequencyWithstandVol | Double | 230kV
| DurationofShortCircuit_s | Double | 3
| RatedShortCircuitBreakCur_kA | Double | 40kA
| RatedLineChargingCurrent_A | Double | 50kA
| RatedShortCircuitMakCurrent_A | Double | 100A
| Rated_Operating_Sequence | Text | O-0.3s-CO-3min-CO
| RatedSF6GasPressure_MPa | Double | 0.74MPa
| RatedMotorVoltage_VDC | Double | 110V
| RatedSupplyVoltageofAuxCirc | Double | 110V
| RatedSupplyVoltClosOpDevice | Double | 110V
| MaximumBreakingTime_ms | Double | 50m
| MaximumMakingTime_ms | Double | 70m
| NumberofTrippingCoils | Short Integer | 1
| NumberofClosingCoils | Short Integer | 1
| NumberofOperations | Short Integer | 10000
| TemperatureRange | Double
| ProtectionClass | Text | IP55
| AltitudeLevel | Double | 2000
| FirstPoleToClearFactor | Double | 1.5
| Operating_Mechanism | Text | Remote ( Relay) - Spring - Manual | 5
| OutofPhaseBreakingCurrent | Double | 10kA
| Owner | Short Integer | REG
| TotalMassCircuitbreaker_kg | Double | 1534kg
| TotalMassofInsulatingMed | Double | 10kg
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-11
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-12
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-21
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-22
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 1
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-2
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-31
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-32
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-3
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-41
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-42
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-51
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-52
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-5
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-61
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-62
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-6
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-71
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-72
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q9-7
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | YES | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-81
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-82
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 220kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-91
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 1
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
High Voltage Switch/High Voltage Switch | Composite_ID | Text
| HV_Switch_ID | Text | Q1-92
| Substation | Text | RBSR-038
| Type | Short Integer | Center break | 1
| FunctionType | Short Integer | Busbar | 2
| Manufacturer | Text | ALSTHOM
| CountryOfManufacturer | Text | INDIA
| ManufacturerYear | Short Integer | 2018
| Standard_Code | Text | IEC 62271-102
| Rated_current_A | Double | 1250A
| Operating_Voltage_kV | Double | 110kV
| EarthingSwitch | Short Integer | NO | 0
| Auxiliary_Contact_vol_Rating | Double | 110V DC
| Auxiliary_Contact_Curr_Rating | Double | 10A
| Motor_Drive | Short Integer | YES | 1
| Motor_Type | Short Integer | DC | 1
| Motor_Voltage_V | Double | 110V DC
| Rated_Peak_Short_Cir_Current | Double | 80kA
Uninterruptable power supply(UPS) | Manufacturer | Text | Not existing
| Substation_ID | Text | Not existing
| CountryOfManufacturer | Text | Not existing
| Applicable_Standard | Text | Not existing
| Model | Text | Not existing
| RatedPoweratAmbientTemp | Double | Not existing
| PowerSupply | Text | Not existing
| ActivePower_Min_kW | Double | Not existing
| TypeofCooling | Short Integer | Not existing
| Protection_class_cubicle | Text | Not existing
| Rated_DC_VoltageInput | Double | Not existing
| RatedVoltageOutput | Double | Not existing
| Frequency_Hz | Short Integer | Not existing
| Maximum_power_loss_rated_load | Double | Not existing
| Total_Weight | Double | Not existing
Substation/Cabin | Substation_Name | Short Integer | RWABUSORO
| Substation_ID | Text | RBSR-038
| Substation_Total_Capacity_MVA | Double | 118.8MVA
| Substation_Voltage_Level_kV | Short Integer | 220/110/30kV | 9
| SubstationArrangement | Short Integer | Switching Substation | 1
| Number_of_Power_Transformers | Short Integer | 2
| Numbe_of_Earthing_Transfomer | Short Integer | 1
| Number_Distribution_Transf | Short Integer | 0
| Number of auxiliary transformers | Short Integer | 0 | 1
| Standby_Generators | Short Integer | No
| Busbar_Configuration_HV | Short Integer | Double busbar | 1
| Number of MV Feeders | Short Integer | 0
| Number of HV line Bays | Short Integer | 6
| Number of Trx Bays | Short Integer | 2
| Configuration_Busbar_MV | Short Integer | Not Existing | 0
| BuscouplerHV | Short Integer | YES | 0
| BuscouplerMV | Short Integer | Not Existing | 1
| Type_of_Busbar_HV | Short Integer | Tubular | 1
| Type_of_MV_switchgears | Short Integer | Not Existing | 1
| Year of Commissioning | Short Integer | 2018
| Year_of_upgrade | Short Integer | NA
| Contractor_Name | Text | STEG INTERNATIONAL
| Substation_Meter_SN | Text | NA
| Lightning_protection | Short Integer | YES | 1
| OperatorsLivingHouse | Short Integer | YES | 0
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276976
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276975
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA2-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276974
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276977
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276978
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA3-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276979
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276980
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276981
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA4-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276982
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276983
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276984
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA5-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276985
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA6-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276986
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA6-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276987
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA6-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276988
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA7-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276989
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA7-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276990
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA7-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276991
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | SIEMENS
| ArresterID | Text | SA8-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2023
| SerialNumber | Text | URG/23020317
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | SIEMENS
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | SIEMENS
| ArresterID | Text | SA8-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2023
| SerialNumber | Text | URG/23020318
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | SIEMENS
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | SIEMENS
| ArresterID | Text | SA8-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | CHINA
| ManufacturerYear | Text | 2023
| SerialNumber | Text | URG/23020319
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 110kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | SIEMENS
| Country_orgin_Dis_Counter | Text | CHINA
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA9-1
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276992
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA9-2
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276993
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
Lightning Arrester | Manufacturer | Short Integer | TRIDELTA
| ArresterID | Text | SA9-3
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | GERMANY
| ManufacturerYear | Text | 2018
| SerialNumber | Text | 276994
| Standard Code | Text | IEC 60099
| FunctionType | Short Integer | Line | 1
| Type_Surge_Arrester | Short Integer | Metal Oxide Varistor | 1
| Power_Frequency_Voltage_kV | Double | 275kV
| MaxContinuousOperatVolt_kV | Double | 190kV
| RatedVoltage_kV1 | Double | 220kV
| NominalDischargeCurrent_kA | Double | 10kA
| Rated_short_circuit_Current | Double | 31.5kA
| Light_Impulse_Withsand_kV | Double | 950kV
| PowerFrequencyWithstandVol | Double | 275kV
| RatedContinuousContinuous_kv | Double | 195kV
| DischargeCounter | Short Integer | YES | 1
| manufacturer_Disch_Counter | Text | TRIDELTA
| Country_orgin_Dis_Counter | Text | GERMANY
| TypeDischargeCounter | Text | DCC-M2
| CounterIndicDischargeCounter | Short Integer | Analog | 2
| ProtClassDischargeCounter | Text | IP55
DC Supply 48 VDC Battery | Manufacturer | Text | SAFT (NIFE)
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | SWEDEN
| Type | Short Integer | NiCd | 1
| Standards_ | Text | IEC 60439/60947
| BatteryFloatingVoltage | Double | 50V
| RatedVoltage | Double | 48V
| TenHrsRatingCapacity | Double | 80Ah
| One_min_rating_Current_A | Double | 120A
| MaximumVolatge_V | Double | 48+15%
| MinimumVoltage_V | Double | 48-15%
| MinimumVoltageperCell | Double | 1.2V
| NumberofCells | Short Integer | 40
| BatteryFloatingVoltage | Double | 50
| BoostChargingVoltage | Double | 55.8V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 60A
| SelfDischargeat_25oC | Double | 7%
| TypeofCooling | Text | Natural
| Charging time (hrs) | Double | 5hrs
DC Supply 110 VDC Battery | Manufacturer | Text | SAFT (NIFE)
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | SWEDEN
| Model | Text | KM300P
| Type | Short Integer | NiCd
| Standards_ | Text | IEC 60623
| RatedVoltage | Double | 110V
| TenHrsRatingCapacity | Double | 300Ah
| One_min_rating_Current_A | Double | 200A
| MaximumVolatge_V | Double | 110+15%
| MinimumVoltage_V | Double | 110-15%
| MinimumVoltageperCell | Double | 2V
| Number_of_cells__No_ | Long Integer | 56
| BatteryFloatingVoltage | Double | 112.5V
| BoostChargingVoltage | Double | 132.3V
| FloatChargeCurrent_A | Double | 6.2A
| BoostChargeCurrent | Double | 300A
| TypeofCooling | Short Integer | Natural
DC Supply 48 VDC charger | Manufacturer | Text | EFAPOWER
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | PORTUGAL
| Model | Text | CIBS 48/ 8*20A
| Charger_type | Short Integer | Thyristor controlled | 2
| Standards_ | Short Integer | DIN41773
| Frequency_Hz | Short Integer | 50Hz | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 8.6kVA
| DC Output (Kw) | Double | 6.8kW
| DC_Output_kV | Double | 48V
| Rated_output_Voltage_V | Double | 48V
| Insulation | Text
| MinInsulationResistance_MΩ | Double | 5MΏ
| OperatingConditions | Text
| Altitude_m | Double | 2000m
| Degree_protection_ | Short Integer | IP 20 | 55
| DCDistributionBoard | Short Integer | No | 0
| RatedCurrent_A | Double | NA
| NumberofFeeders | Short Integer | NA
| short_circuit_capacity_breaker | Double | NA
DC Supply 110 VDC charger | Manufacturer | Text | EFAPOWER
| Substation_ID | Text | RBSR-038
| CountryOfManufacturer | Text | PORTUGAL
| Model | Text | CIBS 110/ 8*20A
| TypeofOperation | Short Integer | Parallel
| Charger_type | Short Integer | THYROTRONIC
| Standards_ | Text | IEC 61000-6-4
| ChargingTime | Double | 5h
| Frequency_Hz | Short Integer | 50
| AC_Supply_V_ | Double | 400V
| Rated_InputPower_kVA | Double | 17.3kVA
| VoltageVariation | Double | ±5%
| DC_Output_kV | Double | 110V
| TypeofCharging | Text | Float/ Boost
| Rated_output_Voltage_V | Double | 110V
| MaximumDC_Voltage_V | Double | 126V
| ConstantVoltageAccuracy | Double | ±10%
| Rated_DC_output_Current_A | Double | 100A
| FloatingVoltageRegulatin | Double | 104.4V
| EqualisingVoltageRegulatin | Double | 128.8V
| Minimum_Insulation_resistance_ | Double | 5MΏ
| TypeofCooling | Short Integer | Natural self-ventilating, Others
| Ambient_temperature | Double | 0°C to +40°C
| Altitude_m | Double | >1000m
| Total_Weight_Charger_kg | Double | 340kg
| Degree_protection_ | Short Integer | IP20
| RatedCurrent_A | Double | 100A
| ShortCircuitStrength_kA_sec | Double | Not provided
| BusbarMaterial | Short Integer | Copper tin-plate, Others
DIGITAL fault recorder | Manufacturer | Text | GENERAL ELECTRIC
| Country_Manufacture | Text | FRANCE
| Type | Text | REASON DR60
| Standards | Text | IEC61850
| Arrangement | Short Integer | Panel mounted | 2
| VT_CT_Connection | Short Integer | Yes | 1
| Frequency_Hz | Short Integer | 50Hz | 50
| Nominal_input_current_A | Double | 1-5A
| Nominal_voltage_Vdc | Double | 110DC
| Power_consumption_VA | Double | 150VA
| NumberofAnalogInputs | Short Integer | 32
| NumberofBinaryInputs | Short Integer | 96
| NumberofBinaryOutputs | Short Integer | 48
| Surge_withstand_capability_KV_ | Double
| Operating_temperature_oC | Double
High Voltage Line | Name | Text | MAMBA 1
| Year_of_commisioning | Short Integer | 2019
| ContractorName | Text | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV
| CondustorSize | Short Integer | 240/40 | 4
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 21.5km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 69.44kN
| MaxElectricResitance | Double | 0.1937(Ω/km)
| PositiveSequenceReactance | Double | 0.437(Ω/km)
| PositiveSequenceResistance | Double | 0.231(Ω/km)
| ZeroSequenceResistance | Double | 0.554(Ω/km)
| ZeroSequenceReactance | Double | 1.430(Ω/km)
| ZeroSequenceCapacitance | Double | 0.01(µF)
| PositiveSequenceCapacitance | Double | 0.0066(µF)
High Voltage Line | Name | Text | MAMBA 2
| Year_of_commisioning | Short Integer | 2019
| ContractorName | Text | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 21.5km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 69.44kN
| MaxElectricResitance | Double | 0.1937(Ω/km)
| PositiveSequenceReactance | Double | 0.437(Ω/km)
| PositiveSequenceResistance | Double | 0.231(Ω/km)
| ZeroSequenceResistance | Double | 0.554(Ω/km)
| ZeroSequenceReactance | Double | 1.430(Ω/km)
| ZeroSequenceCapacitance | Double | 0.01(µF)
| PositiveSequenceCapacitance | Double | 0.0066(µF)
High Voltage Line | Name | Text | KIGOMA
| Year_of_commisioning | Short Integer | Not yet construced
| ContractorName | Text | Not yet construced
| Manufacturer | Text | Not yet construced
| Voltage_Level_kV | Short Integer | Not yet construced | 110
| CondustorSize | Short Integer | Not yet construced | 4
| ShieldWire | Short Integer | Not yet construced | 1
| ConductorType | Short Integer | Not yet construced | 1
| Conductor_type_UG | Text | Not yet construced
| Underground_Cable_Size | Text | Not yet construced | 0
| Underground_Cable_Size | Short Integer | Not yet construced
| UG_Length_Km | Double | Not yet construced
| Length_of_the_Line_ | Double | Not yet construced
| CurrentCarryingCapacity | Double | Not yet construced
| NominalBreakingLoad_KN | Double | Not yet construced
| MaxElectricResitance | Double | Not yet construced
| PositiveSequenceReactance | Double | Not yet construced
| PositiveSequenceResistance | Double | Not yet construced
| ZeroSequenceResistance | Double | Not yet construced
| ZeroSequenceReactance | Double | Not yet construced
| ZeroSequenceCapacitance | Double | Not yet construced
| PositiveSequenceCapacitance | Double | Not yet construced
High Voltage Line | Name | Text | BUGESERA 1
| Year_of_commisioning | Short Integer | 2019
| ContractorName | Text | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 39.6km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 69.44kN
| MaxElectricResitance | Double | 0.1937(Ω/km)
| PositiveSequenceReactance | Double | 0.437(Ω/km)
| PositiveSequenceResistance | Double | 0.231(Ω/km)
| ZeroSequenceResistance | Double | 0.554(Ω/km)
| ZeroSequenceReactance | Double | 1.430(Ω/km)
| ZeroSequenceCapacitance | Double | 0.01(µF)
| PositiveSequenceCapacitance | Double | 0.0066(µF)
High Voltage Line | Name | Text | BUGESERA 2
| Year_of_commisioning | Short Integer | 2019
| ContractorName | Text | STEG INTERNATIONAL
| Manufacturer | Text
| Voltage_Level_kV | Short Integer | 220kV | 110
| CondustorSize | Short Integer | 240/40 | 6
| ShieldWire | Short Integer | OPGW | 1
| ConductorType | Short Integer | ACSR | 1
| Conductor_type_UG | Text
| Underground_Cable_Size | Text | No | 0
| Underground_Cable_Size | Short Integer | NA
| UG_Length_Km | Double | NA
| Length_of_the_Line_ | Double | 39.6km
| CurrentCarryingCapacity | Double | 40MW
| NominalBreakingLoad_KN | Double | 69.44kN
| MaxElectricResitance | Double | 0.1937(Ω/km)
| PositiveSequenceReactance | Double | 0.437(Ω/km)
| PositiveSequenceResistance | Double | 0.231(Ω/km)
| ZeroSequenceResistance | Double | 0.554(Ω/km)
| ZeroSequenceReactance | Double | 1.430(Ω/km)
| ZeroSequenceCapacitance | Double | 0.01(µF)
| PositiveSequenceCapacitance | Double | 0.0066(µF)
Transformer Bay | Trx_Bay_ID | Text | D04
| Substation_ID | Text | RBSR-038
| Trx_Bay_Name | Text | TRANSFORMER 1
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 220kV | 2
| Trx_Bay_Capacity_MVA | Double | 98.3MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | EFACEC TPU T500
| Type_of_Back_up_relay | Text | SIEMENS 7UT613
| Type_of_BCU_Bay_control_unit | Text | EFACEC BCU500
Transformer Bay | Trx_Bay_ID | Text | D08
| Substation_ID | Text | RBSR-038
| Trx_Bay_Name | Text | TRANSFORMER 2
| Bay_Meter_Serial_Number | Text | Not existing
| VoltageLevel_kV | Long Integer | 110kV | 2
| Trx_Bay_Capacity_MVA | Double | 25MVA
| Frequency_Hz | Short Integer | 50Hz | 50
| Type_of_Trx_Differencial_relay | Text | EFACEC TPU T500
| Type_of_Back_up_relay | Text | SIEMENS 7UT613
| Type_of_BCU_Bay_control_unit | Text | EFACEC BCU500
Indoor Circuit Breaker/30kv/15kb | Manufacturer | Text | Note Existing
| CircuitBreakerID | Text | Note Existing
| CountryOfManufacturer | Text | Note Existing
| Type__model | Text | Note Existing
| Standard | Text | Note Existing
| CombinedEArthBusbarDisc | Short Integer | Note Existing | 1
| ArcQuenchingMedium | Short Integer | Note Existing | 2
| Number_phases | Long Integer | Note Existing
| RatedVoltage_kV1 | Double | Note Existing
| MaxContinuousOperatVolt_kV | Double | Note Existing
| RatedImpulseWithstandVol | Double | Note Existing
| PowerFrequencyWithstandVol | Double | Note Existing
| Rated_Frequency | Short Integer | Note Existing | 50
| Rated_short_time_withstand_current__kA_ | Text | Note Existing
| Rated_Peak_Short_Cir_Current | Double | Note Existing
| RatedNormalCurrent_A | Double | Note Existing
| RatedShortCircuitBreakCur_kA | Double | Note Existing
| RatedShortCircuitMakCurrent_A | Double | Note Existing
| RatedCableChargingBreakingCur | Double | Note Existing
| MaximumCApacitivBreakingCur | Double | Note Existing
| Rated_Operating_Sequence | Text | Note Existing
| ClosingTime_ms | Double | Note Existing
| DeadTime_ms | Double | Note Existing
| BreakTime_ms | Double | Note Existing
| MakeTime_ms | Double | Note Existing
| ArcingTime_ms | Double | Note Existing
| AtRAtedContinuousCurrent | Double | Note Existing
| AtRAtedBreakingCurrent | Double | Note Existing
| NumberofNO | Short Integer | Note Existing
| NumberofNc | Short Integer | Note Existing
| RatedMotorVoltage_VDC | Double | Note Existing
| NumberofMakingCoils | Short Integer | Note Existing
| NumberofTrippingCoils | Short Integer | Note Existing
| Volatge_VDC | Double | Note Existing
| PowerSupply | Short Integer | Note Existing
| HandOperatingFacility | Short Integer | Note Existing | 1
Indoor Current Transformer | Manufacturer | Text | Note Existing
| CurrentTransfomer_ID | Text | Note Existing
Note Existing
| CountryOfManufacturer | Text | Note Existing
| Type__model | Text | Note Existing
| Standard | Text | Note Existing
| RatedVoltage_kV1 | Double | Note Existing
| Rated_Frequency | Short Integer | Note Existing | 50
| Number_phases | Long Integer | Note Existing
| NumberofCores | Short Integer | Note Existing
| Rated_Primary_Current_A | Double | Note Existing
| Rated_Secondary_Current | Double | Note Existing
| AccuracyClass | Text | Note Existing
| Burden_VA | Double | Note Existing
| RatedShortTimeWithstandCur | Double | Note Existing
| Rated_Peak_Short_Cir_Current | Double | Note Existing
| RatedImpulseWithstandVol | Double | Note Existing
| LimitsContPrimaryCurrency_A | Double | Note Existing
Indoor Voltage Transformer | Manufacturer | Text | Note Existing
| VoltageTransfomer_ID | Text | Note Existing
Note Existing
| CountryOfManufacturer | Text | Note Existing
| Standard | Text | Note Existing
| TypeofVoltageTransformer | Short Integer | Note Existing
| Rated_Frequency | Short Integer | Note Existing | 50
| Number_phases | Long Integer | Note Existing
| PowerFrequencyWithstandVol | Double | Note Existing
| RatedImpulseWithstandVol | Double | Note Existing
| RatedPrimaryVoltage_kV | Double | Note Existing
| Rated_secondary_voltage_winding_1__V_ | Text | Note Existing
| Rated_secondary_voltage_winding_2__V_ | Text | Note Existing
| Accuracy_class__measuring_ | Text | Note Existing
| Accuracy_class__protection_ | Text | Note Existing
| RatedOutput_VA | Double | Note Existing
| TertiaryVoltage_kV | Long Integer | Note Existing
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-1-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | D02
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D02
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-2-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | D03
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D03
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-3-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | D05
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D02
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-4-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | D06
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D06
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-5-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | D07
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D07
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Control and Protection Panels | Standards | Text | Stand alone
| Control_Protection_Panel_ID | Text | TSP-CPR-6-038
| Substation_ID | Text | RBSR-038
| Bay_ID | Text | E02
| ProtectionClass | Text | IP 65
| PreWired | Short Integer | Yes | 1
| FloorMounted | Short Integer | Yes | 1
| StainlessSteelSheetThickness | Double | 2.5mm
| Max_height_mm | Double | 2000mm
| MaxWidth_mm | Double | 1500mm
| MaxDepth | Double | 2500mm
| FrontdoorMaterial | Text | Steel
| Colouring | Text | RAL 7035
| LineProtectionRelay | Short Integer | EFACEC TPU D500
Distance Protection | RelayType | Text | SIEMENS 7SA87
| Bay_ID | Text | D07
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Rated_Current | Double | 1-5A
| Rated_Voltage | Double | 100-110V
| Number_Phases | Short Integer | 3
| Frequency_Hz | Short Integer | 50Hz | 50
| RangeofAuxilliaryDCSupply_VDC | Double | 110V DC
| QtyofOutputRelaysorContact | Short Integer | 23
| QtyofLEDsforIndications | Short Integer | 14
| System_Interface | Text | Fiber optic
Transformer Protection | RelayType | Text | EFACEC TPU T500
| Bay_ID | Text | D04
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | EFACEC
| Country_manufacturer_ | Text | PORTUGAL
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Transformer Protection | RelayType | Text | EFACEC TPU T500
| Bay_ID | Text | E01
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | EFACEC
| Country_manufacturer_ | Text | PORTUGAL
| SecondaryCurrent_A | Short Integer | 1-5A
| Frequency_Hz | Short Integer | 50Hz | 50
| DC_Supply_V | Double | 110V
| FronSerialInterfaceCom | Text | RS485
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | D02
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | D03
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | D05
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | D06
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | D07
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Line Overcurrent Protection | RelayType | Text | EFACEC TPU S430
| Bay_ID | Text | E02
| Substatoin_ID | Text | RBSR-038
| Manufacturer | Text | SIEMENS
| Country_manufacturer_ | Text | GERMANY
| Frequency_Hz | Short Integer | 50Hz | 50
| Phase current (A) |  | 1-5A
| Phase to phase voltage (V) |  | 100-110V AC
| Auxiliary voltage (V DC) |  | 110V DC
| System_Interface | Text | Fiber optic
| Connection | Text | ST
| Protocol | Text | IEC 60870-5-103
Standby Generator | Manufacturer | Text | GREEN POWER
| Substation_ID | Text | MMBA-041
| Standby_Generator_ID | Text | DGU-1-041
| CountryOfManufacturer | Text | ITALY
| Mode_Operation | Short Integer | Prime / Standby
| Model | Text | GP165 S/I-N-A
| Type_Assembly | Short Integer | Generating set ISO 8528
| Arrangement | Short Integer | Canopy type
| Phases | Short Integer | 3
| RatedOuptuPower_kVA | Double | 220kVA
| RatedVoltage | Double | 230/400V
| RatedCurrent_A | Double | 289A
| PowerFactor | Double | 0.8
| CouplingofEngine | Text | Direct
| FuelLevelEmissionPerm | Double
| DieselEngineType | Text | Perkins
| Governor | Text | PID
| GobernorBrand | Text | Datakom (DKG)
| RatedPower_kVA_kW | Double | 200kVA
| CompressionRatio_ | Text | 15:01
| NoofCylinder | Short Integer | 6
| Speed_RPM | Double | 1500
| Applicable_Standard | Text
| SpeedREgulation | Short Integer
| Fuel_Tank_Capacity | Double | 500L
| Cooling_System | Short Integer | Liquid -cooled closed loup
| NoiseatFullLoad | Double | 96dB
| LubricationOilConsumption | Double | 0.025L/h
| Ambient_temperature | Double | Minus 20 0C up to Plus 40 0C
| Protection index | Text | IP44
| MethodofStarting | Text | Man/Auto
| Voltage_VDC | Double | 24V
| Power_kW | Double | 160kW
| Battery_Capacity_Ah | Double | 135Ah
| BatteryType | Text | Lead-acid
| BrandandModelofBattery | Text
| Frequency_Hz | Short Integer | 50Hz | 50
| VoltageRegulationMode | Short Integer | AVR
| Total_Weight | Double | 2110kg